## APPE
Location | Test Type | Test Number | Test Date-Time | Sys/Comp Info | Severity | EASEY Result Code | Fired | EASEY Result | Notes | Command Line Parameters
ORIS 7277 (Lincoln Combustion Turbine) Location 1 | APPE | 01NOX2021-2 | 2021-02-05 15:26 | 400 (NOX) | CRIT1 | APPE-2-B | Fired | According to your monitoring plan, the Appendix E test was not conducted for a NOXE system. |  | QAT "MDC-A176443524F0445CA3FDB90DB059D5A5" "L3FY866-950F544520244336B5ED7E3824642F9E"
ORIS 7277 (Lincoln Combustion Turbine) Location 1 | APPE | 01NOX2021-2 | 2021-02-05 15:26 | 400 (NOX) | CRIT1 | APPE-42-A | Fired | You have included Appendix E runs at fewer than four operating levels. Appendix E tests for units subject to Part 75 must be performed at at least four operating levels. |  | QAT "MDC-A176443524F0445CA3FDB90DB059D5A5" "L3FY866-950F544520244336B5ED7E3824642F9E"
ORIS 7277 (Lincoln Combustion Turbine) Location 1 | APPE | 01NOX2021-2 | 2021-02-05 15:26 | 400 (NOX) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-A176443524F0445CA3FDB90DB059D5A5" "L3FY866-950F544520244336B5ED7E3824642F9E"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2016-1 | 2016-02-29 16:10 | 410 (NOXE) | CRIT1 | APPE-34-A | Fired | You did not provide GasVolume, which is required for Operating Level 1 Run Number 1 Gas System ID 200. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-E2DCE14FE50F4F0AAABD80F18E8AF17F"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2016-1 | 2016-02-29 16:10 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-E2DCE14FE50F4F0AAABD80F18E8AF17F"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2016-2 | 2016-03-01 15:50 | 400 (NOXE) | CRIT1 | APPE-33-C | Fired | The heat input recalculated from the values reported in the oil record for Operating Level 1 Run Number 1 Oil System ID 100 does not equal the reported OilHeatInput. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-E0FCD2FF894643D88AF758E14D965725"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2016-2 | 2016-03-01 15:50 | 400 (NOXE) | CRIT1 | APPE-37-A | Fired | The reported TotalHeatInput is not consistent with the value recalculated from the Appendix E oil and gas records for Operating Level 1 Run Number 1. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-E0FCD2FF894643D88AF758E14D965725"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2016-2 | 2016-03-01 15:50 | 400 (NOXE) | CRIT1 | APPE-41-A | Fired | The AverageHourlyHeatInputRate reported for Operating Level 1 is inconsistent with the value recalculated from the run and fuel data for the operating level. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-E0FCD2FF894643D88AF758E14D965725"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2016-2 | 2016-03-01 15:50 | 400 (NOXE) | CRIT1 | APPE-44-A | Fired | The HourlyHeatInputRate for Operating Level 1 Run Number 1 does not correspond to the hourly heat input rate recalculated from the start and end times and heat input derived from the Appendix E gas and oil records. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-E0FCD2FF894643D88AF758E14D965725"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2016-2 | 2016-03-01 15:50 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-E0FCD2FF894643D88AF758E14D965725"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2021-1 | 2021-03-01 15:19 | 410 (NOXE) | CRIT1 | APPE-35-B | Fired | You defined an invalid GasGCV for Operating Level 1 Run Number 1 Gas System ID 200. This value must be greater than zero and less than 20,000. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-ECAB6DD9A6A74F3592BAE5FB6CDFCDA0"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2021-1 | 2021-03-01 15:19 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-ECAB6DD9A6A74F3592BAE5FB6CDFCDA0"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2021-1 | 2021-03-01 15:19 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-ECAB6DD9A6A74F3592BAE5FB6CDFCDA0"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2021-1 | 2021-03-01 15:19 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-ECAB6DD9A6A74F3592BAE5FB6CDFCDA0"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2021-2 | 2021-03-02 14:39 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-4E70B5D3137D43C99C8D9F8DBB0CB256"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2021-2 | 2021-03-02 14:39 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-4E70B5D3137D43C99C8D9F8DBB0CB256"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2021-2 | 2021-03-02 14:39 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-4E70B5D3137D43C99C8D9F8DBB0CB256"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2021-2 | 2021-03-02 14:39 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-4E70B5D3137D43C99C8D9F8DBB0CB256"
ORIS 7277 (Lincoln Combustion Turbine) Location 10 | APPE | 10NOX2021-2 | 2021-03-02 14:39 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1C6562D5CFDF461F96E243C11FE2909B" "L3FY866-4E70B5D3137D43C99C8D9F8DBB0CB256"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2016-1 | 2016-02-24 15:43 | 410 (NOXE) | CRIT1 | APPE-41-A | Fired | The AverageHourlyHeatInputRate reported for Operating Level 1 is inconsistent with the value recalculated from the run and fuel data for the operating level. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-795C18A6E7854D06AA05D987F4214144"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2016-1 | 2016-02-24 15:43 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-795C18A6E7854D06AA05D987F4214144"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2016-2 | 2016-02-25 17:45 | 400 (NOXE) | CRIT1 | APPE-39-A | Fired | This test included one or more runs with an HourlyHeatInputRate which is greater than or equal to the HourlyHeatInputRate for a run for a higher operating level. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-4A16646AEC974F6896051A8A1809AA8E"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2016-2 | 2016-02-25 17:45 | 400 (NOXE) | CRIT1 | APPE-41-A | Fired | The AverageHourlyHeatInputRate reported for Operating Level 1 is inconsistent with the value recalculated from the run and fuel data for the operating level. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-4A16646AEC974F6896051A8A1809AA8E"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2016-2 | 2016-02-25 17:45 | 400 (NOXE) | CRIT1 | APPE-44-A | Fired | The HourlyHeatInputRate for Operating Level 1 Run Number 1 does not correspond to the hourly heat input rate recalculated from the start and end times and heat input derived from the Appendix E gas and oil records. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-4A16646AEC974F6896051A8A1809AA8E"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2016-2 | 2016-02-25 17:45 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-4A16646AEC974F6896051A8A1809AA8E"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | CRIT1 | APPE-10-A | Fired | You reported a test BeginDate, BeginHour, and BeginMinute that is not the same as the BeginDate, BeginHour, and BeginMinute of the first run in the Appendix E test. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-6F7C35ABEAB34B2ABAC92C0E15A57437"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | CRIT1 | APPE-42-A | Fired | You have included Appendix E runs at fewer than four operating levels. Appendix E tests for units subject to Part 75 must be performed at at least four operating levels. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-6F7C35ABEAB34B2ABAC92C0E15A57437"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-6F7C35ABEAB34B2ABAC92C0E15A57437"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-6F7C35ABEAB34B2ABAC92C0E15A57437"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-6F7C35ABEAB34B2ABAC92C0E15A57437"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-6F7C35ABEAB34B2ABAC92C0E15A57437"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-6F7C35ABEAB34B2ABAC92C0E15A57437"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | CRIT1 | APPE-34-B | Fired | You defined an invalid GasVolume for Operating Level 1 Run Number 1 Gas System ID 200. This value must be greater than zero and less than 20,000. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-CAC592FD56DB4AF88D90C3324F030DEC"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | CRIT1 | APPE-35-B | Fired | You defined an invalid GasGCV for Operating Level 1 Run Number 1 Gas System ID 200. This value must be greater than zero and less than 20,000. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-CAC592FD56DB4AF88D90C3324F030DEC"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | CRIT1 | APPE-36-B | Fired | You defined an invalid GasHeatInput for Operating Level 1 Run Number 1 Gas System ID 200. This value must be greater than zero and less than 20,000. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-CAC592FD56DB4AF88D90C3324F030DEC"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | CRIT1 | APPE-43-A | Fired | You have defined an inconsistent number of fuel flow records for this test. There must be the same combination of supporting fuel flow records for each run. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-CAC592FD56DB4AF88D90C3324F030DEC"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-CAC592FD56DB4AF88D90C3324F030DEC"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-CAC592FD56DB4AF88D90C3324F030DEC"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-CAC592FD56DB4AF88D90C3324F030DEC"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-CAC592FD56DB4AF88D90C3324F030DEC"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-CAC592FD56DB4AF88D90C3324F030DEC"
ORIS 7277 (Lincoln Combustion Turbine) Location 11 | APPE | 11NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-258F49D01A2243D2802D18F2D1E43DC6" "L3FY866-CAC592FD56DB4AF88D90C3324F030DEC"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2016-1 | 2016-02-24 15:43 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-E625E98720174A3E961083FA1597B738"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2016-2 | 2016-02-25 17:45 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-F22C51A8FFDB4ED1BEE4222F05D51787"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-6F26E7E3492E477DAB41DBA90A7905ED"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-6F26E7E3492E477DAB41DBA90A7905ED"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-6F26E7E3492E477DAB41DBA90A7905ED"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-6F26E7E3492E477DAB41DBA90A7905ED"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-6F26E7E3492E477DAB41DBA90A7905ED"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-1 | 2021-02-24 14:31 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-6F26E7E3492E477DAB41DBA90A7905ED"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | CRIT1 | APPE-6-A | Fired | The OilVolumeUnitsOfMeasure in the oil flow records for MonitoringSystemID(s) CAMD-2C756C36CD5A4A48B59BAE65BCB7D081 are inconsistent. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-DC25A6F66CE943A8B547084CA20F140D"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | CRIT1 | APPE-26-B | Fired | You reported a value for OilVolume and/or OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 1 Run Number 1 Oil System ID 100. You must not report a value in this field if you are using an OILM system. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-DC25A6F66CE943A8B547084CA20F140D"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-DC25A6F66CE943A8B547084CA20F140D"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-DC25A6F66CE943A8B547084CA20F140D"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-DC25A6F66CE943A8B547084CA20F140D"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-DC25A6F66CE943A8B547084CA20F140D"
ORIS 7277 (Lincoln Combustion Turbine) Location 12 | APPE | 12NOX2021-2 | 2021-02-25 14:42 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-08A627843CA346F78C527084F53BD125" "L3FY866-DC25A6F66CE943A8B547084CA20F140D"
ORIS 7277 (Lincoln Combustion Turbine) Location 13 | APPE | 13NOX2016-1 | 2016-02-23 15:30 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-46D057EEA7954C3DBC60BA19EB02928D" "L3FY866-B5C05B477EEB44F29E47066CAE348586"
ORIS 7277 (Lincoln Combustion Turbine) Location 13 | APPE | 13NOX2016-2 | 2016-02-22 18:29 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-46D057EEA7954C3DBC60BA19EB02928D" "L3FY866-15A679252B2F494B91F98B232BFDC995"
ORIS 7277 (Lincoln Combustion Turbine) Location 13 | APPE | 13NOX2021-1 | 2021-02-22 15:12 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-46D057EEA7954C3DBC60BA19EB02928D" "L3FY866-2ED0537D9D89473D8A878B77A6663D3C"
ORIS 7277 (Lincoln Combustion Turbine) Location 13 | APPE | 13NOX2021-1 | 2021-02-22 15:12 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-46D057EEA7954C3DBC60BA19EB02928D" "L3FY866-2ED0537D9D89473D8A878B77A6663D3C"
ORIS 7277 (Lincoln Combustion Turbine) Location 13 | APPE | 13NOX2021-1 | 2021-02-22 15:12 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-46D057EEA7954C3DBC60BA19EB02928D" "L3FY866-2ED0537D9D89473D8A878B77A6663D3C"
ORIS 7277 (Lincoln Combustion Turbine) Location 13 | APPE | 13NOX2021-2 | 2021-02-23 15:07 | 400 (NOXE) | CRIT1 | APPE-52-A | Fired | You have not defined a maximum NOx emission rate default value for the fuel to be used for missing data purposes in the monitoring plan. |  | QAT "MDC-46D057EEA7954C3DBC60BA19EB02928D" "L3FY866-BE0F1C05B15749CC9DB5DA599767A561"
ORIS 7277 (Lincoln Combustion Turbine) Location 13 | APPE | 13NOX2021-2 | 2021-02-23 15:07 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-46D057EEA7954C3DBC60BA19EB02928D" "L3FY866-BE0F1C05B15749CC9DB5DA599767A561"
ORIS 7277 (Lincoln Combustion Turbine) Location 13 | APPE | 13NOX2021-2 | 2021-02-23 15:07 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-46D057EEA7954C3DBC60BA19EB02928D" "L3FY866-BE0F1C05B15749CC9DB5DA599767A561"
ORIS 7277 (Lincoln Combustion Turbine) Location 13 | APPE | 13NOX2021-2 | 2021-02-23 15:07 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-46D057EEA7954C3DBC60BA19EB02928D" "L3FY866-BE0F1C05B15749CC9DB5DA599767A561"
ORIS 7277 (Lincoln Combustion Turbine) Location 13 | APPE | 13NOX2021-2 | 2021-02-23 15:07 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-46D057EEA7954C3DBC60BA19EB02928D" "L3FY866-BE0F1C05B15749CC9DB5DA599767A561"
ORIS 7277 (Lincoln Combustion Turbine) Location 14 | APPE | 14NOX2016-1 | 2016-02-23 15:30 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-CCB6A5CB4DFA4857989C77FEC6F87E79" "L3FY866-9730C8CF2BC548E1A7D71814932D815E"
ORIS 7277 (Lincoln Combustion Turbine) Location 14 | APPE | 14NOX2016-2 | 2016-02-22 18:29 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-CCB6A5CB4DFA4857989C77FEC6F87E79" "L3FY866-A8A5C1BEFA4D49798E0949EFF4B86830"
ORIS 7277 (Lincoln Combustion Turbine) Location 14 | APPE | 14NOX2021-1 | 2021-02-22 15:12 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-CCB6A5CB4DFA4857989C77FEC6F87E79" "L3FY866-1401E7F738CF4E12BF9A4D1413121F18"
ORIS 7277 (Lincoln Combustion Turbine) Location 14 | APPE | 14NOX2021-1 | 2021-02-22 15:12 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-CCB6A5CB4DFA4857989C77FEC6F87E79" "L3FY866-1401E7F738CF4E12BF9A4D1413121F18"
ORIS 7277 (Lincoln Combustion Turbine) Location 14 | APPE | 14NOX2021-1 | 2021-02-22 15:12 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-CCB6A5CB4DFA4857989C77FEC6F87E79" "L3FY866-1401E7F738CF4E12BF9A4D1413121F18"
ORIS 7277 (Lincoln Combustion Turbine) Location 14 | APPE | 14NOX2021-2 | 2021-02-23 15:07 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-CCB6A5CB4DFA4857989C77FEC6F87E79" "L3FY866-DBA18B850022414BA8A18338F3E11A73"
ORIS 7277 (Lincoln Combustion Turbine) Location 14 | APPE | 14NOX2021-2 | 2021-02-23 15:07 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-CCB6A5CB4DFA4857989C77FEC6F87E79" "L3FY866-DBA18B850022414BA8A18338F3E11A73"
ORIS 7277 (Lincoln Combustion Turbine) Location 14 | APPE | 14NOX2021-2 | 2021-02-23 15:07 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-CCB6A5CB4DFA4857989C77FEC6F87E79" "L3FY866-DBA18B850022414BA8A18338F3E11A73"
ORIS 7277 (Lincoln Combustion Turbine) Location 14 | APPE | 14NOX2021-2 | 2021-02-23 15:07 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-CCB6A5CB4DFA4857989C77FEC6F87E79" "L3FY866-DBA18B850022414BA8A18338F3E11A73"
ORIS 7277 (Lincoln Combustion Turbine) Location 14 | APPE | 14NOX2021-2 | 2021-02-23 15:07 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-CCB6A5CB4DFA4857989C77FEC6F87E79" "L3FY866-DBA18B850022414BA8A18338F3E11A73"
ORIS 7277 (Lincoln Combustion Turbine) Location 14 | APPE | 14NOX2021-2 | 2021-02-23 15:07 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-CCB6A5CB4DFA4857989C77FEC6F87E79" "L3FY866-DBA18B850022414BA8A18338F3E11A73"
ORIS 7277 (Lincoln Combustion Turbine) Location 15 | APPE | 15NOX2016-1 | 2016-02-17 16:11 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-C727D8EEE28644C4936CD8D6CE0E5A0D" "L3FY866-B213444877B04B5CB59D10594C631840"
ORIS 7277 (Lincoln Combustion Turbine) Location 15 | APPE | 15NOX2016-2 | 2016-02-18 16:03 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-C727D8EEE28644C4936CD8D6CE0E5A0D" "L3FY866-2D07875ECFA64ED2945E2AE24610F76A"
ORIS 7277 (Lincoln Combustion Turbine) Location 15 | APPE | 15NOX2021-1 | 2021-02-17 14:52 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-C727D8EEE28644C4936CD8D6CE0E5A0D" "L3FY866-F697C3B45E974F04AB31B3E74A6BE5BB"
ORIS 7277 (Lincoln Combustion Turbine) Location 15 | APPE | 15NOX2021-1 | 2021-02-17 14:52 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-C727D8EEE28644C4936CD8D6CE0E5A0D" "L3FY866-F697C3B45E974F04AB31B3E74A6BE5BB"
ORIS 7277 (Lincoln Combustion Turbine) Location 15 | APPE | 15NOX2021-1 | 2021-02-17 14:52 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-C727D8EEE28644C4936CD8D6CE0E5A0D" "L3FY866-F697C3B45E974F04AB31B3E74A6BE5BB"
ORIS 7277 (Lincoln Combustion Turbine) Location 15 | APPE | 15NOX2021-1 | 2021-02-17 14:52 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-C727D8EEE28644C4936CD8D6CE0E5A0D" "L3FY866-F697C3B45E974F04AB31B3E74A6BE5BB"
ORIS 7277 (Lincoln Combustion Turbine) Location 15 | APPE | 15NOX2021-2 | 2021-02-18 14:46 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-C727D8EEE28644C4936CD8D6CE0E5A0D" "L3FY866-E9C448C0A77E4626BF434B9B8EF765EA"
ORIS 7277 (Lincoln Combustion Turbine) Location 15 | APPE | 15NOX2021-2 | 2021-02-18 14:46 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-C727D8EEE28644C4936CD8D6CE0E5A0D" "L3FY866-E9C448C0A77E4626BF434B9B8EF765EA"
ORIS 7277 (Lincoln Combustion Turbine) Location 15 | APPE | 15NOX2021-2 | 2021-02-18 14:46 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-C727D8EEE28644C4936CD8D6CE0E5A0D" "L3FY866-E9C448C0A77E4626BF434B9B8EF765EA"
ORIS 7277 (Lincoln Combustion Turbine) Location 15 | APPE | 15NOX2021-2 | 2021-02-18 14:46 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-C727D8EEE28644C4936CD8D6CE0E5A0D" "L3FY866-E9C448C0A77E4626BF434B9B8EF765EA"
ORIS 7277 (Lincoln Combustion Turbine) Location 15 | APPE | 15NOX2021-2 | 2021-02-18 14:46 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-C727D8EEE28644C4936CD8D6CE0E5A0D" "L3FY866-E9C448C0A77E4626BF434B9B8EF765EA"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2016-1 | 2016-02-17 16:11 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-31417F60B6AF42798884FC1A40210EAE"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2016-2 | 2016-02-18 16:03 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-8930EFD12AF346889A8DAD72817BF727"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2021-1 | 2021-02-17 14:52 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-05850343BDB342B8B700ED3A95086442"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2021-1 | 2021-02-17 14:52 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-05850343BDB342B8B700ED3A95086442"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2021-1 | 2021-02-17 14:52 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-05850343BDB342B8B700ED3A95086442"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2021-1 | 2021-02-17 14:52 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-05850343BDB342B8B700ED3A95086442"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2021-1 | 2021-02-17 14:52 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-05850343BDB342B8B700ED3A95086442"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2021-1 | 2021-02-17 14:52 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-05850343BDB342B8B700ED3A95086442"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2021-2 | 2021-02-18 14:46 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-F2224DF3AA6F4946AE29A5D996EEF9E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2021-2 | 2021-02-18 14:46 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-F2224DF3AA6F4946AE29A5D996EEF9E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2021-2 | 2021-02-18 14:46 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-F2224DF3AA6F4946AE29A5D996EEF9E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2021-2 | 2021-02-18 14:46 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-F2224DF3AA6F4946AE29A5D996EEF9E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 16 | APPE | 16NOX2021-2 | 2021-02-18 14:46 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-D020B3B742D24E4EBCEE0224833BA04B" "L3FY866-F2224DF3AA6F4946AE29A5D996EEF9E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2016-1 | 2016-02-04 15:46 | 410 (NOXE) | CRIT1 | APPE-38-A | Fired | The Appendix E test contains fewer than three run records for Operating Level 1. A minimum of three runs are required at each operating level. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-23B302662BC64DBFB302453845190917"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2016-1 | 2016-02-04 15:46 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-23B302662BC64DBFB302453845190917"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2016-2 | 2016-03-02 09:00 | 400 (NOXE) | CRIT1 | APPE-7-A | Fired | One or more runs in this test have overlapping run times. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-DFFB47D96F2D4411A36EC22A8F6C7CBA"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2016-2 | 2016-03-02 09:00 | 400 (NOXE) | CRIT1 | APPE-8-A | Fired | There are missing or non-sequential OperatingLevelForRun and RunNumbers in this test. Run numbers must begin with 1 and be consecutive within the entire test or within each operating level. The lowest OperatingLevelForRun must be equal to 1. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-DFFB47D96F2D4411A36EC22A8F6C7CBA"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2016-2 | 2016-03-02 09:00 | 400 (NOXE) | CRIT1 | APPE-43-A | Fired | You have defined an inconsistent number of fuel flow records for this test. There must be the same combination of supporting fuel flow records for each run. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-DFFB47D96F2D4411A36EC22A8F6C7CBA"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2016-2 | 2016-03-02 09:00 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-DFFB47D96F2D4411A36EC22A8F6C7CBA"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-1 | 2021-02-04 16:06 | 410 (NOXE) | CRIT1 | APPE-7-A | Fired | One or more runs in this test have overlapping run times. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-F08BD23613E44D8AB3E99B692F8AA9D6"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-1 | 2021-02-04 16:06 | 410 (NOXE) | CRIT1 | APPE-41-A | Fired | The AverageHourlyHeatInputRate reported for Operating Level 1 is inconsistent with the value recalculated from the run and fuel data for the operating level. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-F08BD23613E44D8AB3E99B692F8AA9D6"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-1 | 2021-02-04 16:06 | 410 (NOXE) | CRIT1 | APPE-44-A | Fired | The HourlyHeatInputRate for Operating Level 1 Run Number 2 does not correspond to the hourly heat input rate recalculated from the start and end times and heat input derived from the Appendix E gas and oil records. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-F08BD23613E44D8AB3E99B692F8AA9D6"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-1 | 2021-02-04 16:06 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-F08BD23613E44D8AB3E99B692F8AA9D6"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-1 | 2021-02-04 16:06 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-F08BD23613E44D8AB3E99B692F8AA9D6"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-1 | 2021-02-04 16:06 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-F08BD23613E44D8AB3E99B692F8AA9D6"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-1 | 2021-02-04 16:06 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-F08BD23613E44D8AB3E99B692F8AA9D6"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-2 | 2021-02-05 15:26 | 400 (NOXE) | CRIT1 | APPE-3-A | Fired | You did not provide TestReasonCode, which is required for this test. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-0ED3C130B5664239BEFE5FD6211F2613"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-2 | 2021-02-05 15:26 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-0ED3C130B5664239BEFE5FD6211F2613"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-2 | 2021-02-05 15:26 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-0ED3C130B5664239BEFE5FD6211F2613"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-2 | 2021-02-05 15:26 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-0ED3C130B5664239BEFE5FD6211F2613"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-2 | 2021-02-05 15:26 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-0ED3C130B5664239BEFE5FD6211F2613"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-2 | 2021-02-05 15:26 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-0ED3C130B5664239BEFE5FD6211F2613"
ORIS 7277 (Lincoln Combustion Turbine) Location 2 | APPE | 02NOX2021-2 | 2021-02-05 15:26 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EB1F6B20B4EB4A6BA4EA355F28622030" "L3FY866-0ED3C130B5664239BEFE5FD6211F2613"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2016-1 | 2016-02-08 17:34 | 410 (NOXE) | CRIT1 | APPE-10-A | Fired | You reported a test BeginDate, BeginHour, and BeginMinute that is not the same as the BeginDate, BeginHour, and BeginMinute of the first run in the Appendix E test. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-F8C2ACF7054342EB92A221DD3017769A"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2016-1 | 2016-02-08 17:34 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-F8C2ACF7054342EB92A221DD3017769A"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2016-2 | 2016-02-10 16:21 | 400 (NOXE) | CRIT1 | APPE-11-A | Fired | You reported an EndDate, EndHour, and EndMinute for the Appendix E test that is not the same as the EndDate, EndHour, and EndMinute of the last run in the test. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-6D992D3D006A4D5F9CE7102BED75AFBD"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2016-2 | 2016-02-10 16:21 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-6D992D3D006A4D5F9CE7102BED75AFBD"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | FATAL |  | Fired | Failed executing method 'AppendixE40'. Index was outside the bounds of the array. at ECMPS.Checks.AppendixEChecks.cAppendixEChecks.AppendixE40(cCategory Category, Boolean& Log) in C:\Dev\CAMDDevelopment\easey-quartz-scheduler\CheckEngine\QA\Checks\AppendixEChecks.cs:line 1596
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | FATAL |  | Fired | Failed executing method 'AppendixE41'. Index was outside the bounds of the array. at ECMPS.Checks.AppendixEChecks.cAppendixEChecks.AppendixE41(cCategory Category, Boolean& Log) in C:\Dev\CAMDDevelopment\easey-quartz-scheduler\CheckEngine\QA\Checks\AppendixEChecks.cs:line 1650
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | CRIT1 | APPE-13-B | Fired | The value in the field OperatingLevelForRun for Operating Level -1 is not within the range of valid values from 1 to 99. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-736FF933262E47EA8E0E33EA485CAFD5"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | CRIT1 | APPE-38-A | Fired | The Appendix E test contains fewer than three run records for Operating Level -1. A minimum of three runs are required at each operating level. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-736FF933262E47EA8E0E33EA485CAFD5"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-736FF933262E47EA8E0E33EA485CAFD5"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-736FF933262E47EA8E0E33EA485CAFD5"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-736FF933262E47EA8E0E33EA485CAFD5"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-736FF933262E47EA8E0E33EA485CAFD5"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-736FF933262E47EA8E0E33EA485CAFD5"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-2 | 2021-02-09 15:28 | 400 (NOXE) | CRIT1 | APPE-14-C | Fired | The value 3.100 in the field MeanReferenceValue for Operating Level 1 is not within the range of valid values from 0 to 3. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-5BD424738C9A4FBE97864C8A8F580B23"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-2 | 2021-02-09 15:28 | 400 (NOXE) | CRIT1 | APPE-40-A | Fired | The MeanReferenceValue reported for Operating Level 1 is inconsistent with the value recalculated from the run data for the test. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-5BD424738C9A4FBE97864C8A8F580B23"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-2 | 2021-02-09 15:28 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-5BD424738C9A4FBE97864C8A8F580B23"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-2 | 2021-02-09 15:28 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-5BD424738C9A4FBE97864C8A8F580B23"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-2 | 2021-02-09 15:28 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-5BD424738C9A4FBE97864C8A8F580B23"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-2 | 2021-02-09 15:28 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-5BD424738C9A4FBE97864C8A8F580B23"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-2 | 2021-02-09 15:28 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-5BD424738C9A4FBE97864C8A8F580B23"
ORIS 7277 (Lincoln Combustion Turbine) Location 3 | APPE | 03NOX2021-2 | 2021-02-09 15:28 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-636EF828194B4705B8FCAE7960338471" "L3FY866-5BD424738C9A4FBE97864C8A8F580B23"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2016-1 | 2016-02-08 17:34 | 410 (NOXE) | CRIT1 | APPE-15-B | Fired | The value 0.0 in the field FFactor for Operating Level 1 is not within the range of valid values from 1000 to 22000. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-D079C0B39AB6447B86A1A2B194D2D153"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2016-1 | 2016-02-08 17:34 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-D079C0B39AB6447B86A1A2B194D2D153"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2016-2 | 2016-02-09 16:21 | 400 (NOXE) | CRIT1 | APPE-9-A | Fired | The test was conducted at the same time as another Appendix E test for MonitoringSystemID 400. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-3BB7C50CF3884BC1A0A1DB499E83DE6F"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2016-2 | 2016-02-09 16:21 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-3BB7C50CF3884BC1A0A1DB499E83DE6F"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | CRIT1 | APPE-16-A | Fired | You did not provide AverageHourlyHeatInputRate, which is required for Operating Level 1. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-F51B23BE281F45F58AC0595D02E6D1DF"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-F51B23BE281F45F58AC0595D02E6D1DF"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-F51B23BE281F45F58AC0595D02E6D1DF"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-F51B23BE281F45F58AC0595D02E6D1DF"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-F51B23BE281F45F58AC0595D02E6D1DF"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-F51B23BE281F45F58AC0595D02E6D1DF"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-1 | 2021-02-08 16:44 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-F51B23BE281F45F58AC0595D02E6D1DF"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT1 | AETB-9-B | Fired | You reported an ExamDate that is after the date of the test for Dustin E. Banks. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT1 | APPE-9-A | Fired | The test was conducted at the same time as another Appendix E test for MonitoringSystemID 400. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT1 | APPE-10-A | Fired | You reported a test BeginDate, BeginHour, and BeginMinute that is not the same as the BeginDate, BeginHour, and BeginMinute of the first run in the Appendix E test. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT1 | APPE-11-A | Fired | You reported an EndDate, EndHour, and EndMinute for the Appendix E test that is not the same as the EndDate, EndHour, and EndMinute of the last run in the test. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT1 | PGVP-3-F | Fired | You have reported a vendor for Cylinder Identifier CC417166, but this vendor was not active at the time of this test. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT1 | PGVP-3-F | Fired | You have reported a vendor for Cylinder Identifier CC417166, but this vendor was not active at the time of this test. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT1 | PGVP-3-F | Fired | You have reported a vendor for Cylinder Identifier CC704813, but this vendor was not active at the time of this test. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT1 | PGVP-3-F | Fired | You have reported a vendor for Cylinder Identifier CC704813, but this vendor was not active at the time of this test. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT1 | PGVP-3-F | Fired | You have reported a vendor for Cylinder Identifier CC416465, but this vendor was not active at the time of this test. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT1 | PGVP-3-F | Fired | You have reported a vendor for Cylinder Identifier CC254003, but this vendor was not active at the time of this test. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT2 | PGVP-4-D | Fired | You reported an ExpirationDate for the cylinder that is more than eight years after the date of the test for Cylinder Identifier CC417166. Gas cylinders expire in less than eight years. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT2 | PGVP-4-D | Fired | You reported an ExpirationDate for the cylinder that is more than eight years after the date of the test for Cylinder Identifier CC417166. Gas cylinders expire in less than eight years. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT2 | PGVP-4-D | Fired | You reported an ExpirationDate for the cylinder that is more than eight years after the date of the test for Cylinder Identifier CC704813. Gas cylinders expire in less than eight years. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT2 | PGVP-4-D | Fired | You reported an ExpirationDate for the cylinder that is more than eight years after the date of the test for Cylinder Identifier CC704813. Gas cylinders expire in less than eight years. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT2 | PGVP-4-D | Fired | You reported an ExpirationDate for the cylinder that is more than eight years after the date of the test for Cylinder Identifier CC254003. Gas cylinders expire in less than eight years. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | CRIT2 | PGVP-4-D | Fired | You reported an ExpirationDate for the cylinder that is more than eight years after the date of the test for Cylinder Identifier CC416465. Gas cylinders expire in less than eight years. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 4 | APPE | 04NOX2021-2 | 2016-02-09 15:28 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-502E7EDB89B045AD85E33474AD02F553" "L3FY866-96850CEE05794B07A6E130073D4FE3E7"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2016-1 | 2016-02-10 00:30 | 410 (NOXE) | CRIT1 | APPE-8-A | Fired | There are missing or non-sequential OperatingLevelForRun and RunNumbers in this test. Run numbers must begin with 1 and be consecutive within the entire test or within each operating level. The lowest OperatingLevelForRun must be equal to 1. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-0B6EE1EB17DD4C09B59B1EBA2EB8A68D"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2016-1 | 2016-02-10 00:30 | 410 (NOXE) | CRIT1 | APPE-11-A | Fired | You reported an EndDate, EndHour, and EndMinute for the Appendix E test that is not the same as the EndDate, EndHour, and EndMinute of the last run in the test. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-0B6EE1EB17DD4C09B59B1EBA2EB8A68D"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2016-1 | 2016-02-10 00:30 | 410 (NOXE) | CRIT1 | APPE-18-B | Fired | You defined an invalid RunNumber for Operating Level 1 Run Number 0. This value must be greater than zero and less than 20,000. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-0B6EE1EB17DD4C09B59B1EBA2EB8A68D"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2016-1 | 2016-02-10 00:30 | 410 (NOXE) | CRIT1 | APPE-43-A | Fired | You have defined an inconsistent number of fuel flow records for this test. There must be the same combination of supporting fuel flow records for each run. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-0B6EE1EB17DD4C09B59B1EBA2EB8A68D"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2016-1 | 2016-02-10 00:30 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-0B6EE1EB17DD4C09B59B1EBA2EB8A68D"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2016-2 | 2016-02-11 15:59 | 400 (NOXE) | CRIT1 | APPE-19-A | Fired | The BeginDate, BeginHour, and/or BeginMinute for Operating Level 1 Run Number 1 is invalid. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-65A8B7EACB304E6CB942A8DE049A7EE0"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2016-2 | 2016-02-11 15:59 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-65A8B7EACB304E6CB942A8DE049A7EE0"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2021-1 | 2021-02-10 14:49 | 410 (NOXE) | CRIT1 | APPE-20-A | Fired | The EndDate, EndHour, and/or EndMinute for Operating Level 1 Run Number 1 are invalid. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-C8982F6BD345448483D02A93CDA82B75"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2021-1 | 2021-02-10 14:49 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-C8982F6BD345448483D02A93CDA82B75"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2021-1 | 2021-02-10 14:49 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-C8982F6BD345448483D02A93CDA82B75"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2021-1 | 2021-02-10 14:49 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-C8982F6BD345448483D02A93CDA82B75"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2021-2 | 2021-02-11 15:20 | 400 (NOXE) | CRIT1 | APPE-21-A | Fired | The value -1 in the field ResponseTime for Operating Level 1 Run Number 1 is not within the range of valid values from 0 to 800. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-8113681D36884A2FB54AB124FF00AD45"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2021-2 | 2021-02-11 15:20 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-8113681D36884A2FB54AB124FF00AD45"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2021-2 | 2021-02-11 15:20 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-8113681D36884A2FB54AB124FF00AD45"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2021-2 | 2021-02-11 15:20 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-8113681D36884A2FB54AB124FF00AD45"
ORIS 7277 (Lincoln Combustion Turbine) Location 5 | APPE | 05NOX2021-2 | 2021-02-11 15:20 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-E3CAEF0BF9B84EFDB67860DE9B25C3C1" "L3FY866-8113681D36884A2FB54AB124FF00AD45"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2016-1 | 2016-02-10 15:52 | 410 (NOXE) | CRIT1 | APPE-22-A | Fired | You did not provide ReferenceValue, which is required for Operating Level 1 Run Number 1. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-84AA30AD3B9040FD898D06922D9B120F"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2016-1 | 2016-02-10 15:52 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-84AA30AD3B9040FD898D06922D9B120F"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2016-2 | 2016-02-11 15:59 | 400 (NOXE) | CRIT1 | APPE-23-B | Fired | You defined an invalid HourlyHeatInputRate for Operating Level 1 Run Number 1. This value must be greater than zero and less than 20,000. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-866688F14D4444C2BC9085593AEC595B"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2016-2 | 2016-02-11 15:59 | 400 (NOXE) | CRIT1 | APPE-41-A | Fired | The AverageHourlyHeatInputRate reported for Operating Level 1 is inconsistent with the value recalculated from the run and fuel data for the operating level. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-866688F14D4444C2BC9085593AEC595B"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2016-2 | 2016-02-11 15:59 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-866688F14D4444C2BC9085593AEC595B"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2021-1 | 2021-02-10 14:49 | 410 (NOXE) | CRIT1 | APPE-24-B | Fired | You defined an invalid TotalHeatInput for Operating Level 1 Run Number 1. This value must be greater than zero and less than 20,000. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-7E72EB18CFF94E10AC2678C0C7D70E05"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2021-1 | 2021-02-10 14:49 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-7E72EB18CFF94E10AC2678C0C7D70E05"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2021-1 | 2021-02-10 14:49 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-7E72EB18CFF94E10AC2678C0C7D70E05"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2021-1 | 2021-02-10 14:49 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-7E72EB18CFF94E10AC2678C0C7D70E05"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2021-1 | 2021-02-10 14:49 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-7E72EB18CFF94E10AC2678C0C7D70E05"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2021-1 | 2021-02-10 14:49 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-7E72EB18CFF94E10AC2678C0C7D70E05"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2021-2 | 2021-02-11 15:20 | 400 (NOXE) | CRIT1 | APPE-26-B | Fired | You reported a value for OilVolume and/or OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 1 Run Number 1 Oil System ID 100. You must not report a value in this field if you are using an OILM system. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-3C3EE44F659E4DE5B9BCB1C47BA3186B"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2021-2 | 2021-02-11 15:20 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-3C3EE44F659E4DE5B9BCB1C47BA3186B"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2021-2 | 2021-02-11 15:20 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-3C3EE44F659E4DE5B9BCB1C47BA3186B"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2021-2 | 2021-02-11 15:20 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-3C3EE44F659E4DE5B9BCB1C47BA3186B"
ORIS 7277 (Lincoln Combustion Turbine) Location 6 | APPE | 06NOX2021-2 | 2021-02-11 15:20 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-EBE2CA86EDD540F689466D33B808C12C" "L3FY866-3C3EE44F659E4DE5B9BCB1C47BA3186B"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2016-1 | 2016-02-15 17:52 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-FA035178F7F84A88B218A965C0BFFACB"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-31-A | Fired | You did not provide OilGCVUnitsOfMeasureCode, which is required for Operating Level 1 Run Number 1 Oil System ID 100. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-7BD4AE3EE07144BF962B2343819D64EB"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-7BD4AE3EE07144BF962B2343819D64EB"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-1 | 2021-02-15 15:18 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-911C0D04955041B4B4B0B84FEACFE4D3"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-1 | 2021-02-15 15:18 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-911C0D04955041B4B4B0B84FEACFE4D3"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-1 | 2021-02-15 15:18 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-911C0D04955041B4B4B0B84FEACFE4D3"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-1 | 2021-02-15 15:18 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-911C0D04955041B4B4B0B84FEACFE4D3"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-1 | 2021-02-15 15:18 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-911C0D04955041B4B4B0B84FEACFE4D3"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-1 | 2021-02-15 15:18 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-911C0D04955041B4B4B0B84FEACFE4D3"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-1A58F08C59C741E0A7F3EF70BA15A3D9"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-1A58F08C59C741E0A7F3EF70BA15A3D9"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-1A58F08C59C741E0A7F3EF70BA15A3D9"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-1A58F08C59C741E0A7F3EF70BA15A3D9"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-1A58F08C59C741E0A7F3EF70BA15A3D9"
ORIS 7277 (Lincoln Combustion Turbine) Location 7 | APPE | 07NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-1910AE73CCF94788ACC91DBDF04F5D82" "L3FY866-1A58F08C59C741E0A7F3EF70BA15A3D9"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-1 | 2016-02-15 17:52 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-114ED671257B45B4BEE304072877305A"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 1 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 1 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 1 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 2 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 2 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 2 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 3 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 3 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 3 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 4 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 4 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 4 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 1 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 1 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 1 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 2 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 2 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 2 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 3 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 3 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 3 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 4 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 4 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 4 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 1 Run Number 1 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 1 Run Number 2 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 1 Run Number 3 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 2 Run Number 1 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 2 Run Number 2 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 2 Run Number 3 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 3 Run Number 1 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 3 Run Number 2 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 3 Run Number 3 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 4 Run Number 1 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 4 Run Number 2 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 4 Run Number 3 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2016-2 | 2016-02-16 15:42 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-86464D1C941D4D909CA4195D615E7D05"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-1 | 2021-02-15 15:18 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-794D0FCF9D4042959D2AAFA3D27E695C"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-1 | 2021-02-15 15:18 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-794D0FCF9D4042959D2AAFA3D27E695C"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-1 | 2021-02-15 15:18 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-794D0FCF9D4042959D2AAFA3D27E695C"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 3 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 1 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 1 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 1 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 2 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 2 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 2 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 3 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 3 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 4 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 4 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-26-A | Fired | You did not report a value for OilVolume in the oil flow record for Operating Level 4 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 4 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 1 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 1 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 1 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 2 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 2 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 2 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 3 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 3 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 3 Run Number 3 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 4 Run Number 1 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-27-A | Fired | You did not report a value for OilVolumeUnitsOfMeasureCode in the oil flow record for Operating Level 4 Run Number 2 Oil System ID 100. You must report a value in this field when you are using an OILV system. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-28-A | Fired | You did not provide OilDensityUnitsOfMeasureCode, which is required for Operating Level 1 Run Number 1 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 2 Run Number 2 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 1 Run Number 2 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 1 Run Number 3 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 2 Run Number 1 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 2 Run Number 3 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 3 Run Number 1 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 3 Run Number 2 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 3 Run Number 3 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 4 Run Number 1 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 4 Run Number 2 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-B | Fired | You did not provide OilDensity, which is required for Operating Level 4 Run Number 3 Oil System ID 100. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | CRIT1 | APPE-29-C | Fired | You defined an invalid OilDensity for Operating Level 1 Run Number 1 Oil System ID 100. This value must be greater than zero and less than 20,000. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 8 | APPE | 08NOX2021-2 | 2021-02-16 15:25 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-B0650B6F966941238CCBCF3C9880ED9E" "L3FY866-F5C5BE5DBA4A42DD8913AF592D664E72"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2016-1 | 2016-02-29 16:10 | 410 (NOXE) | CRIT1 | APPE-36-A | Fired | You did not provide GasHeatInput, which is required for Operating Level 1 Run Number 1 Gas System ID 200. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-96C41AEB42524B86B7D3F6ADFB1C56CB"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2016-1 | 2016-02-29 16:10 | 410 (NOXE) | CRIT1 | APPE-37-A | Fired | The reported TotalHeatInput is not consistent with the value recalculated from the Appendix E oil and gas records for Operating Level 1 Run Number 1. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-96C41AEB42524B86B7D3F6ADFB1C56CB"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2016-1 | 2016-02-29 16:10 | 410 (NOXE) | CRIT1 | APPE-41-A | Fired | The AverageHourlyHeatInputRate reported for Operating Level 1 is inconsistent with the value recalculated from the run and fuel data for the operating level. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-96C41AEB42524B86B7D3F6ADFB1C56CB"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2016-1 | 2016-02-29 16:10 | 410 (NOXE) | CRIT1 | APPE-44-A | Fired | The HourlyHeatInputRate for Operating Level 1 Run Number 1 does not correspond to the hourly heat input rate recalculated from the start and end times and heat input derived from the Appendix E gas and oil records. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-96C41AEB42524B86B7D3F6ADFB1C56CB"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2016-1 | 2016-02-29 16:10 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-96C41AEB42524B86B7D3F6ADFB1C56CB"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2016-2 | 2016-03-01 15:50 | 400 (NOXE) | CRIT1 | APPE-30-A | Fired | You did not report a value for OilMass in the oil flow record for Operating Level 1 Run Number 1 Oil System ID 100. You must report a value for OilMass when you are using an OILM system. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-61DD3355CC8442DB8A9D3F9B96EE22C7"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2016-2 | 2016-03-01 15:50 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-61DD3355CC8442DB8A9D3F9B96EE22C7"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2021-1 | 2021-03-01 15:19 | 410 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-26629F73869C4AF29FC6854DBED6B4B6"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2021-1 | 2021-03-01 15:19 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-26629F73869C4AF29FC6854DBED6B4B6"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2021-1 | 2021-03-01 15:19 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-26629F73869C4AF29FC6854DBED6B4B6"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2021-1 | 2021-03-01 15:19 | 410 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-26629F73869C4AF29FC6854DBED6B4B6"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2021-2 | 2021-03-02 14:39 | 400 (NOXE) | CRIT1 | APPE-32-B | Fired | You defined an invalid OilGCV for Operating Level 1 Run Number 1 Oil System ID 100. This value must be greater than zero and less than 20,000. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-09B9B4D14DA04657ABE81C38A7A4B5F7"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2021-2 | 2021-03-02 14:39 | 400 (NOXE) | INFORM | APPE-4-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-09B9B4D14DA04657ABE81C38A7A4B5F7"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2021-2 | 2021-03-02 14:39 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-09B9B4D14DA04657ABE81C38A7A4B5F7"
ORIS 7277 (Lincoln Combustion Turbine) Location 9 | APPE | 09NOX2021-2 | 2021-03-02 14:39 | 400 (NOXE) | NONE | PGVP-14-A | Fired | You reported the same Cylinder Identifier for more than one protocol gas cylinder. |  | QAT "MDC-5175C17CDA2D4D528B3FDBDC2ED6E126" "L3FY866-09B9B4D14DA04657ABE81C38A7A4B5F7"

## F2LCHK
Location | Test Type | Test Number | Test Date-Time | Sys/Comp Info | Severity | EASEY Result Code | Fired | EASEY Result | Notes | Command Line Parameters
ORIS 130 (Cross) Location 1 | F2LCHK | 400-43 |  | 004 (FLOW) | NONCRIT | F2LCHK-17-F | Fired | The TestResultCode is equal to "FAILED", but the AvgAbsolutePercentDiff indicates that the test passed the applicable standard based on the RATA load level reported in the flow to load reference record and the use of bias adjusted or non-adjusted values. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-0031EAFF04C74604A6AA1352D9F7372F"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-43 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-0031EAFF04C74604A6AA1352D9F7372F"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-44 |  | 004 (FLOW) | CRIT1 | F2LCHK-16-A | Fired | You did not provide AvgAbsolutePercentDiff, which is required for this test. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-22058B21D90E44AFA6B8C60ECC80D81C"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-44 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-22058B21D90E44AFA6B8C60ECC80D81C"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-46 |  | 004 (FLOW) | CRIT1 | F2LCHK-15-A | Fired | You reported a TestBasisCode of H in the flow-to-load check, but the software could not find a prior flow-to-load reference data record based on the same criterion. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-73546CFACBBB45EBBF3423734D7800F8"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-46 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-73546CFACBBB45EBBF3423734D7800F8"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-48 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-C8E5A297AC964497879CACF295A51D66"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-50 |  | 004 (FLOW) | CRIT1 | F2LCHK-13-A | Fired | The total number of hours used in the flow-to-load or GHR analysis plus the number of hours excluded exceed the total number of hours in the quarter. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-7A00ED0D78114F288A2384AFE3C5F061"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-50 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-7A00ED0D78114F288A2384AFE3C5F061"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-53 |  | 004 (FLOW) | CRIT1 | F2LCHK-12-A | Fired | The value -1 in the field NumberOfHoursExcMainBypass for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-0A7E507D37E244C6B84674DCCCF9BC60"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-53 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-0A7E507D37E244C6B84674DCCCF9BC60"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-54 |  | 004 (FLOW) | CRIT1 | F2LCHK-11-A | Fired | The value -1 in the field NumberOfHoursExcludedTest for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-A2EDD6C0EAFF43899BC9E788314D4644"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-54 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-A2EDD6C0EAFF43899BC9E788314D4644"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-56 |  | 004 (FLOW) | CRIT1 | F2LCHK-10-A | Fired | The value -1 in the field NumberOfHoursExcludedPreRATA for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-27A9CA0C00B04163A5F75590AAD34CF8"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-56 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-27A9CA0C00B04163A5F75590AAD34CF8"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-58 |  | 004 (FLOW) | CRIT1 | F2LCHK-9-A | Fired | The value -1 in the field NumberOfHoursExcludedBypass for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-AB012341DD4245DE85D743F75F132C77"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-58 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-AB012341DD4245DE85D743F75F132C77"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-61 |  | 004 (FLOW) | CRIT1 | F2LCHK-8-A | Fired | The value -1 in the field NumberOfHoursExcludedRamping for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-F818787E16594A7595A19E4434042086"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-61 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-F818787E16594A7595A19E4434042086"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-63 |  | 004 (FLOW) | CRIT1 | F2LCHK-7-A | Fired | The value -1 in the field NumberOfHoursExcludedForFuel for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-B47E154E104E47A0B918AAFB616AFE8D"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-63 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-B47E154E104E47A0B918AAFB616AFE8D"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-64 |  | 004 (FLOW) | CRIT1 | F2LCHK-5-A | Fired | You did not provide BiasAdjustedIndicator, which is required for this test. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-68E349F4307A4A1E9457B6EB6E69CAED"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-64 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-68E349F4307A4A1E9457B6EB6E69CAED"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-67 |  | 004 (FLOW) | CRIT1 | F2LCHK-6-C | Fired | The NumberOfHours of quality assured flow data exceeds or equals 168 hours. A Flow-to-load analysis or GHR analysis is required for the quarter. Do not report a TestResultCode of 'EXC168H' or 'FEW168H' for this quarter. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-552AFCE983B2490397CA65025AA6F604"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-67 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-552AFCE983B2490397CA65025AA6F604"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-69 |  | 004 (FLOW) | CRIT1 | F2LCHK-4-A | Fired | You did not provide TestBasisCode, which is required for this test. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-41C1C2E05845410E9D8A1A7678AFE45E"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-69 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-41C1C2E05845410E9D8A1A7678AFE45E"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-70 |  | 004 (FLOW) | CRIT1 | F2LCHK-3-A | Fired | You did not provide OperatingLevelCode, which is required for this test. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-6304A9493A2A40F29C9293C14D82D674"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-72 |  | 004 (FLOW) | CRIT1 | F2LCHK-2-A | Fired | You did not provide TestReasonCode, which is required for this test. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-A7455776CE9B4FF587A1032DDC11068F"
ORIS 130 (Cross) Location 1 | F2LCHK | 400-72 |  | 004 (FLOW) | INFORM | F2LCHK-14-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-A7455776CE9B4FF587A1032DDC11068F"
ORIS 2442 (Four Corners Steam Elec Station) Location 4 | F2LCHK | 87 |  | F43 (CO2) | CRIT1 | F2LCHK-1-B | Fired | According to the monitoring system record, the monitoring system in this flow-to-load check was not a flow system. |  | QAT "MDC-D4C88AC0994340F2AB7E9E0DB1EF8FCB" "PC49096-4BA9ED868B7443D3A2FD95BE53CECBA9"
ORIS 2442 (Four Corners Steam Elec Station) Location 4 | F2LCHK | 87 |  | F43 (CO2) | CRIT1 | TEST-22-B | Fired | A Monitoring Plan associated with this test has not been evaluated. You must evaluate all active and future Monitoring Plans containing the location in this test in order to complete the evaluation of this test. |  | QAT "MDC-D4C88AC0994340F2AB7E9E0DB1EF8FCB" "PC49096-4BA9ED868B7443D3A2FD95BE53CECBA9"

## F2LREF
Location | Test Type | Test Number | Test Date-Time | Sys/Comp Info | Severity | EASEY Result Code | Fired | EASEY Result | Notes | Command Line Parameters
ORIS 130 (Cross) Location 1 | F2LREF | 400-32 | 2016-02-11 11:27 | 004 (FLOW) | FATAL | F2LREF-2-D | Fired | Another Certification Test record with this test number has already been submitted for this location. If this is a different test, you must assign it a unique test number. If you wish to edit the existing test, you should import or download the test. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-2FB566F1BACA4A188DD3791B0DD165DA"
ORIS 130 (Cross) Location 1 | F2LREF | 400-32 | 2016-02-11 11:27 | 004 (FLOW) | CRIT1 | F2LREF-13-A | Fired | You defined an invalid ReferenceGrossHeatRate for this test. This value must be greater than zero and less than 20,000. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-2FB566F1BACA4A188DD3791B0DD165DA"
ORIS 130 (Cross) Location 1 | F2LREF | 400-36 | 2017-01-05 06:55 | 004 (FLOW) | CRIT1 | F2LREF-11-A | Fired | You did not provide AverageGrossUnitLoad, which is required for this test. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-51802DAB23C54B86A90276CF664A2225"
ORIS 130 (Cross) Location 1 | F2LREF | 400-36 | 2017-01-05 06:55 | 004 (FLOW) | INFORM | F2LREF-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-51802DAB23C54B86A90276CF664A2225"
ORIS 130 (Cross) Location 1 | F2LREF | 400-38 | 2017-01-04 14:24 | 004 (FLOW) | CRIT1 | F2LREF-12-A | Fired | You defined an invalid ReferenceFlowLoadRatio for this test. This value must be greater than zero and less than 20,000. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-B92A6FE61C614E31B40ACCF8C75FA092"
ORIS 130 (Cross) Location 1 | F2LREF | 400-38 | 2017-01-04 14:24 | 004 (FLOW) | INFORM | F2LREF-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-B92A6FE61C614E31B40ACCF8C75FA092"
ORIS 130 (Cross) Location 1 | F2LREF | 400-44 | 2018-03-27 08:50 | 004 (FLOW) | CRIT1 | F2LREF-8-B | Fired | The reference RATA was performed at different time from the end time reported in the flow-to-load reference data. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-4E5BF3CD209C475ABDE479609ED7D73C"
ORIS 130 (Cross) Location 1 | F2LREF | 400-44 | 2018-03-27 08:50 | 004 (FLOW) | INFORM | F2LREF-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-4E5BF3CD209C475ABDE479609ED7D73C"
ORIS 130 (Cross) Location 1 | F2LREF | 400-45 | 2018-03-26 14:59 | 004 (FLOW) | CRIT1 | F2LREF-10-A | Fired | You did not provide AverageReferenceMethodFlow, which is required for this test. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-D29F19F75A74438FBAA76B1D8A930364"
ORIS 130 (Cross) Location 1 | F2LREF | 400-45 | 2018-03-26 14:59 | 004 (FLOW) | INFORM | F2LREF-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCCANX2FNC-D29F19F75A74438FBAA76B1D8A930364"
ORIS 130 (Cross) Location 1 | F2LREF | 400-52 | 2019-01-30 10:09 | 004 (FLOW) | CRIT1 | F2LREF-6-B | Fired | You reported a value of "1" as the CalcSeparateReferenceIndicator, but this is value is only appropriate for a multiple stack. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-CC8627FD01594CE482B5AD750A1CD844"
ORIS 130 (Cross) Location 1 | F2LREF | 400-52 | 2019-01-30 10:09 | 004 (FLOW) | INFORM | F2LREF-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-CC8627FD01594CE482B5AD750A1CD844"
ORIS 130 (Cross) Location 1 | F2LREF | 400-53 | 2019-01-28 14:44 | 004 (FLOW) | NONCRIT | F2LREF-7-A | Fired | You reported an AverageHourlyHeatInputRate but did not determine the ReferenceGrossHeatRate value. The hourly heat input rate is only needed if you use the GHR methodology. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-9C9E8019A3044880AFBBA14EA7BC1E6E"
ORIS 130 (Cross) Location 1 | F2LREF | 400-53 | 2019-01-28 14:44 | 004 (FLOW) | INFORM | F2LREF-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-9C9E8019A3044880AFBBA14EA7BC1E6E"
ORIS 130 (Cross) Location 1 | F2LREF | 400-64 | 2020-07-03 14:05 | 004 (FLOW) | CRIT1 | F2LREF-4-D | Fired | The OperatingLevelCode is not designated as a normal load level in the active MonitorLoad record. Flow-to-load reference data must be based on the RATA for the normal operating level. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-07ECA534ED4A4B50B94DE487FC072024"
ORIS 130 (Cross) Location 1 | F2LREF | 400-64 | 2020-07-03 14:05 | 004 (FLOW) | INFORM | F2LREF-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-07ECA534ED4A4B50B94DE487FC072024"
ORIS 130 (Cross) Location 1 | F2LREF | 400-65 | 2020-07-03 08:36 | 004 (FLOW) | FATAL | F2LREF-2-D | Fired | Another Certification Test record with this test number has already been submitted for this location. If this is a different test, you must assign it a unique test number. If you wish to edit the existing test, you should import or download the test. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-DF48DF5F54BF446C9CAD7F05FE295EA8"
ORIS 130 (Cross) Location 1 | F2LREF | 400-65 | 2020-07-03 08:36 | 004 (FLOW) | CRIT1 | F2LREF-5-C | Fired | You reported a ReferenceGrossHeatRate value but did not provide the AverageHourlyHeatInputRate. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-DF48DF5F54BF446C9CAD7F05FE295EA8"
ORIS 130 (Cross) Location 1 | F2LREF | 400-70 | 2021-04-29 16:15 | 004 (FLOW) | INFORM | F2LREF-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-11917B3E59334C99BD7F0ECECA2040EB"
ORIS 130 (Cross) Location 1 | F2LREF | 400-71 | 2021-04-28 10:18 | 004 (FLOW) | CRIT1 | F2LREF-3-A | Fired | You did not provide RATATestNumber, which is required for this test. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-9ADD34F690504B2DB0EF6261EBC28476"
ORIS 130 (Cross) Location 1 | F2LREF | 400-71 | 2021-04-28 10:18 | 004 (FLOW) | INFORM | F2LREF-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "MCA2F23LHK-9ADD34F690504B2DB0EF6261EBC28476"
ORIS 130 (Cross) Location 1 | F2LREF | AAA | 2018-04-01 15:59 | 004 (FLOW) | CRIT1 | F2LREF-9-A | Fired | The AverageGrossUnitLoad and AverageReferenceMethodFlow could not be recalculated because of invalid data in the reported reference RATA(s). |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "CHV-SABER-F0098559523641328B59D538A1354863"
ORIS 130 (Cross) Location 1 | RATA | AAA | 2018-04-02 07:50 | 004 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level L, because of the errors listed above. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "CHV-SABER-88B0B970AC8848CD92FCCA64032108E6"
ORIS 130 (Cross) Location 1 | RATA | AAA | 2018-04-02 07:50 | 004 (FLOW) | ADMNOVR | RATA-34-B | Fired | The RATA for Operating Level L contains fewer than nine RATA run records with a run status of "RUNUSED". A minimum of nine runs are required for each complete operating level test. |  | QAT "MDC-3B23A43070D74F53AA2DAD83ABFC190C" "CHV-SABER-88B0B970AC8848CD92FCCA64032108E6"
ORIS 2442 (Four Corners Steam Elec Station) Location 4 | F2LREF | F43-Q2-2021-1 | 2021-06-21 16:38 | F43 (CO2) | CRIT1 | F2LREF-1-B | Fired | According to the monitoring system record, the Flow-to-load reference data was not for a flow system. |  | QAT "MDC-D4C88AC0994340F2AB7E9E0DB1EF8FCB" "PC49096-389AF24B880A4839B7D1041D3B973F5E"
ORIS 2442 (Four Corners Steam Elec Station) Location 4 | F2LREF | F43-Q2-2021-1 | 2021-06-21 16:38 | F43 (CO2) | CRIT1 | TEST-22-B | Fired | A Monitoring Plan associated with this test has not been evaluated. You must evaluate all active and future Monitoring Plans containing the location in this test in order to complete the evaluation of this test. |  | QAT "MDC-D4C88AC0994340F2AB7E9E0DB1EF8FCB" "PC49096-389AF24B880A4839B7D1041D3B973F5E"
ORIS 2442 (Four Corners Steam Elec Station) Location 4 | F2LREF | F43-Q2-2021-1 | 2021-06-21 16:38 | F43 (CO2) | INFORM | F2LREF-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-D4C88AC0994340F2AB7E9E0DB1EF8FCB" "PC49096-389AF24B880A4839B7D1041D3B973F5E"

## FF2LBAS
Location | Test Type | Test Number | Test Date-Time | Sys/Comp Info | Severity | EASEY Result Code | Fired | EASEY Result | Notes | Command Line Parameters
ORIS 56249 (NCEMC Anson Plant) Location ES1-A | FF2LBAS | FF2B-Q32021-01A-1 |  | 01A (CO2) | CRIT1 | FF2LBAS-1-B | Fired | According to the monitoring system record, the monitoring system for this fuel flow-to-load baseline data record was not a fuel flow system. |  | QAT "MDC-F3ED630C7DE34EFA8BB22A34B636F88B" "NC-PORTERK-BDDB557D060C41B8969061D494D92A5C"
ORIS 56249 (NCEMC Anson Plant) Location ES1-A | FF2LBAS | FF2B-Q32021-01A-1 |  | 01A (CO2) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-F3ED630C7DE34EFA8BB22A34B636F88B" "NC-PORTERK-BDDB557D060C41B8969061D494D92A5C"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LBAS | FF2B-Q32016-02A-2 |  | 02A (GAS) | CRIT1 | FF2LBAS-3-A | Fired | You did not provide AccuracyTestNumber, which is required for this test. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-DADB116D7B074BBAB722F6842F5ADA6B"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LBAS | FF2B-Q32016-02A-2 |  | 02A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-DADB116D7B074BBAB722F6842F5ADA6B"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LBAS | FF2B-Q32021-02A-2 |  | 02A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-1C3822E0E2124707BB31B767BC51B2C3"
ORIS 56249 (NCEMC Anson Plant) Location ES2-A | FF2LBAS | FF2B-Q32016-03A-5 |  | 03A (GAS) | CRIT1 | FF2LBAS-14-B | Fired | The number of hours excluded in the baseline data collection period exceeds the number of available clock hours in the period. |  | QAT "MDC-59DA9CEF8EFF42C1B0AE839A5EC7CE35" "NC-PORTERK-C72C82072C444CC79E2F57B6124ED59C"
ORIS 56249 (NCEMC Anson Plant) Location ES2-A | FF2LBAS | FF2B-Q32016-03A-5 |  | 03A (GAS) | CRIT2 | FF2LBAS-5-A | Fired | The baseline period exceeds the 4 quarters allowed for the collection of fuel flow-to-load baseline data. |  | QAT "MDC-59DA9CEF8EFF42C1B0AE839A5EC7CE35" "NC-PORTERK-C72C82072C444CC79E2F57B6124ED59C"
ORIS 56249 (NCEMC Anson Plant) Location ES2-A | FF2LBAS | FF2B-Q32016-03A-5 |  | 03A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-59DA9CEF8EFF42C1B0AE839A5EC7CE35" "NC-PORTERK-C72C82072C444CC79E2F57B6124ED59C"
ORIS 56249 (NCEMC Anson Plant) Location ES2-A | FF2LBAS | FF2B-Q32021-03A-5 |  | 03A (GAS) | CRIT1 | FF2LBAS-4-A | Fired | You reported both a Fuel flow-to-load ratio and a GHR value. Since only one methodology can be used, this record is invalid. |  | QAT "MDC-59DA9CEF8EFF42C1B0AE839A5EC7CE35" "NC-PORTERK-129B38F099274B80A7053461D8763BA9"
ORIS 56249 (NCEMC Anson Plant) Location ES2-A | FF2LBAS | FF2B-Q32021-03A-5 |  | 03A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-59DA9CEF8EFF42C1B0AE839A5EC7CE35" "NC-PORTERK-129B38F099274B80A7053461D8763BA9"
ORIS 56249 (NCEMC Anson Plant) Location ES2-B | FF2LBAS | FF2B-Q32016-04A-6 |  | 04A (GAS) | CRIT1 | FF2LBAS-7-A | Fired | You did not provide AverageLoad, which is required for this test. |  | QAT "MDC-F163EC790F8540589B19A3DA0E8BF3B0" "NC-PORTERK-B224AD762EDB46118555F0DFE79DFFF2"
ORIS 56249 (NCEMC Anson Plant) Location ES2-B | FF2LBAS | FF2B-Q32016-04A-6 |  | 04A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-F163EC790F8540589B19A3DA0E8BF3B0" "NC-PORTERK-B224AD762EDB46118555F0DFE79DFFF2"
ORIS 56249 (NCEMC Anson Plant) Location ES2-B | FF2LBAS | FF2B-Q32021-04A-6 |  | 04A (GAS) | CRIT1 | FF2LBAS-6-B | Fired | The test identified by the PEITestNumber in the fuel flow-to-load baseline data cannot be found. |  | QAT "MDC-F163EC790F8540589B19A3DA0E8BF3B0" "NC-PORTERK-AD7CCF5164084E51AC978D4899FFB061"
ORIS 56249 (NCEMC Anson Plant) Location ES2-B | FF2LBAS | FF2B-Q32021-04A-6 |  | 04A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-F163EC790F8540589B19A3DA0E8BF3B0" "NC-PORTERK-AD7CCF5164084E51AC978D4899FFB061"
ORIS 56249 (NCEMC Anson Plant) Location ES3-A | FF2LBAS | FF2B-Q32021-05A-9 |  | 05A (GAS) | CRIT1 | FF2LBAS-8-A | Fired | You defined an invalid AverageHourlyHeatInputRate for this test. This value must be greater than zero and less than 20,000. |  | QAT "MDC-88DF03257BEB4259A84C621191CD3E90" "NC-PORTERK-F18881D9C17B4853A1310E83776B98F6"
ORIS 56249 (NCEMC Anson Plant) Location ES3-A | FF2LBAS | FF2B-Q32021-05A-9 |  | 05A (GAS) | CRIT1 | FF2LBAS-16-A | Fired | You did not provide GHRUnitsOfMeasureCode, which is required for this test. |  | QAT "MDC-88DF03257BEB4259A84C621191CD3E90" "NC-PORTERK-F18881D9C17B4853A1310E83776B98F6"
ORIS 56249 (NCEMC Anson Plant) Location ES3-A | FF2LBAS | FF2B-Q32021-05A-9 |  | 05A (GAS) | CRIT1 | FF2LBAS-18-A | Fired | You did not provide BaselineGHR, which is required for this test. |  | QAT "MDC-88DF03257BEB4259A84C621191CD3E90" "NC-PORTERK-F18881D9C17B4853A1310E83776B98F6"
ORIS 56249 (NCEMC Anson Plant) Location ES3-A | FF2LBAS | FF2B-Q32021-05A-9 |  | 05A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-88DF03257BEB4259A84C621191CD3E90" "NC-PORTERK-F18881D9C17B4853A1310E83776B98F6"
ORIS 56249 (NCEMC Anson Plant) Location ES3-B | FF2LBAS | FF2B-Q32021-06A-10 |  | 06A (GAS) | CRIT1 | FF2LBAS-9-B | Fired | The AverageHourlyHeatInputRate for the baseline period exceeds the maximum heat input capacity for the unit or for all units linked to the pipe. |  | QAT "MDC-9CAF43DE147D4B728E55A78C7CD13A6B" "NC-PORTERK-549BA80F41EB4783BD70FA9DE2B4F81A"
ORIS 56249 (NCEMC Anson Plant) Location ES3-B | FF2LBAS | FF2B-Q32021-06A-10 |  | 06A (GAS) | CRIT1 | FF2LBAS-16-A | Fired | You did not provide GHRUnitsOfMeasureCode, which is required for this test. |  | QAT "MDC-9CAF43DE147D4B728E55A78C7CD13A6B" "NC-PORTERK-549BA80F41EB4783BD70FA9DE2B4F81A"
ORIS 56249 (NCEMC Anson Plant) Location ES3-B | FF2LBAS | FF2B-Q32021-06A-10 |  | 06A (GAS) | CRIT1 | FF2LBAS-18-A | Fired | You did not provide BaselineGHR, which is required for this test. |  | QAT "MDC-9CAF43DE147D4B728E55A78C7CD13A6B" "NC-PORTERK-549BA80F41EB4783BD70FA9DE2B4F81A"
ORIS 56249 (NCEMC Anson Plant) Location ES3-B | FF2LBAS | FF2B-Q32021-06A-10 |  | 06A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9CAF43DE147D4B728E55A78C7CD13A6B" "NC-PORTERK-549BA80F41EB4783BD70FA9DE2B4F81A"
ORIS 56249 (NCEMC Anson Plant) Location ES4-A | FF2LBAS | FF2B-Q32021-07A-13 |  | 07A (GAS) | CRIT1 | FF2LBAS-10-A | Fired | You defined an invalid AverageFuelFlowRate for this test. This value must be greater than zero and less than 20,000. |  | QAT "MDC-881AA62E471C4F6D86B1C9CF15F9224C" "NC-PORTERK-ADBD6ABAB40542D9B1961F0DF8730411"
ORIS 56249 (NCEMC Anson Plant) Location ES4-A | FF2LBAS | FF2B-Q32021-07A-13 |  | 07A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-881AA62E471C4F6D86B1C9CF15F9224C" "NC-PORTERK-ADBD6ABAB40542D9B1961F0DF8730411"
ORIS 56249 (NCEMC Anson Plant) Location ES4-B | FF2LBAS | FF2B-Q32021-08A-14 |  | 08A (GAS) | CRIT2 | FF2LBAS-11-A | Fired | According to the Accuracy Test (and PEI) associated with the fuel flow-to-load baseline data, the begin date and hour of the baseline data collection period is prior to the date when the accuracy test (and PEI) were completed or the flowmeter was reinstalled. |  | QAT "MDC-9B42B3CE6D7D4F95BD48D5B8413C0FF3" "NC-PORTERK-7F4B3EA6893A42D895ACD7B80D3BDAE3"
ORIS 56249 (NCEMC Anson Plant) Location ES4-B | FF2LBAS | FF2B-Q32021-08A-14 |  | 08A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9B42B3CE6D7D4F95BD48D5B8413C0FF3" "NC-PORTERK-7F4B3EA6893A42D895ACD7B80D3BDAE3"
ORIS 56249 (NCEMC Anson Plant) Location ES4-B | FF2LBAS | FF2B-Q32021-08A-14 |  | 08A (GAS) | INFORM | TEST-21-A | Fired | IMPORTANT FYI: This test was determined to be "INVALID" due to one or more Critical Level 2 errors. The reported data indicate that the test was not performed according to the requirements and therefore cannot be used to validate emissions data. Unless you make corrections to the test data and re-run the evaluation, this test will be disregarded by the emissions evaluation routine. If you are unable to eliminate the Critical Level 2 error(s) by correcting the test data but you believe this test should be considered valid, contact your CAMD analyst. |  | QAT "MDC-9B42B3CE6D7D4F95BD48D5B8413C0FF3" "NC-PORTERK-7F4B3EA6893A42D895ACD7B80D3BDAE3"
ORIS 56249 (NCEMC Anson Plant) Location ES5-A | FF2LBAS | FF2B-Q32021-09A-17 |  | 09A (GAS) | CRIT1 | FF2LBAS-12-A | Fired | The value -1 in the field NumberOfHoursExcludedCofiring for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-72022806AF864AA0BFB5F772EEAE433D" "NC-PORTERK-5DDDEFAB27104DFFA5277B0E38998B18"
ORIS 56249 (NCEMC Anson Plant) Location ES5-A | FF2LBAS | FF2B-Q32021-09A-17 |  | 09A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-72022806AF864AA0BFB5F772EEAE433D" "NC-PORTERK-5DDDEFAB27104DFFA5277B0E38998B18"
ORIS 56249 (NCEMC Anson Plant) Location ES5-B | FF2LBAS | FF2B-Q32016-10A-18 |  | 10A (GAS) | CRIT1 | FF2LBAS-14-A | Fired | The value -1 in the field NumberOfHoursExcludedLowRange for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-6C8FC79314A94DE6973CE3CE0ED87F64" "NC-PORTERK-7D05BA490C0F4F12BD9C5A40EC1EA5DE"
ORIS 56249 (NCEMC Anson Plant) Location ES5-B | FF2LBAS | FF2B-Q32016-10A-18 |  | 10A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-6C8FC79314A94DE6973CE3CE0ED87F64" "NC-PORTERK-7D05BA490C0F4F12BD9C5A40EC1EA5DE"
ORIS 56249 (NCEMC Anson Plant) Location ES5-B | FF2LBAS | FF2B-Q32021-10A-18 |  | 10A (GAS) | CRIT1 | FF2LBAS-13-A | Fired | The value -1 in the field NumberOfHoursExcludedRamping for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-6C8FC79314A94DE6973CE3CE0ED87F64" "NC-PORTERK-DBC1D8DD91F24F82BEE575A32487143E"
ORIS 56249 (NCEMC Anson Plant) Location ES5-B | FF2LBAS | FF2B-Q32021-10A-18 |  | 10A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-6C8FC79314A94DE6973CE3CE0ED87F64" "NC-PORTERK-DBC1D8DD91F24F82BEE575A32487143E"
ORIS 56249 (NCEMC Anson Plant) Location ES6-A | FF2LBAS | FF2B-Q32016-11A-21 |  | 11A (GAS) | CRIT1 | FF2LBAS-16-A | Fired | You did not provide GHRUnitsOfMeasureCode, which is required for this test. |  | QAT "MDC-C00BECCBFFBF4447A2AD4F5C0AD78D3E" "NC-PORTERK-A6CBBF6E5D704B58B44C02B4B0479131"
ORIS 56249 (NCEMC Anson Plant) Location ES6-A | FF2LBAS | FF2B-Q32016-11A-21 |  | 11A (GAS) | CRIT1 | FF2LBAS-18-A | Fired | You did not provide BaselineGHR, which is required for this test. |  | QAT "MDC-C00BECCBFFBF4447A2AD4F5C0AD78D3E" "NC-PORTERK-A6CBBF6E5D704B58B44C02B4B0479131"
ORIS 56249 (NCEMC Anson Plant) Location ES6-A | FF2LBAS | FF2B-Q32016-11A-21 |  | 11A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-C00BECCBFFBF4447A2AD4F5C0AD78D3E" "NC-PORTERK-A6CBBF6E5D704B58B44C02B4B0479131"
ORIS 56249 (NCEMC Anson Plant) Location ES6-A | FF2LBAS | FF2B-Q32021-11A-21 |  | 11A (GAS) | CRIT1 | FF2LBAS-15-A | Fired | You did not provide FuelFlowToLoadUOMCode, which is required for this test. |  | QAT "MDC-C00BECCBFFBF4447A2AD4F5C0AD78D3E" "NC-PORTERK-2BE5688CCFFE4D9FA679FAA5E8E058EC"
ORIS 56249 (NCEMC Anson Plant) Location ES6-A | FF2LBAS | FF2B-Q32021-11A-21 |  | 11A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-C00BECCBFFBF4447A2AD4F5C0AD78D3E" "NC-PORTERK-2BE5688CCFFE4D9FA679FAA5E8E058EC"
ORIS 56249 (NCEMC Anson Plant) Location ES6-B | FF2LBAS | FF2B-Q32016-12A-22 |  | 12A (GAS) | CRIT1 | FF2LBAS-16-A | Fired | You did not provide GHRUnitsOfMeasureCode, which is required for this test. |  | QAT "MDC-F29B1E823FF24AD490BBFEE45079B809" "NC-PORTERK-068C3936ABD442EF84D1CF8999AD9E38"
ORIS 56249 (NCEMC Anson Plant) Location ES6-B | FF2LBAS | FF2B-Q32016-12A-22 |  | 12A (GAS) | CRIT1 | FF2LBAS-18-A | Fired | You did not provide BaselineGHR, which is required for this test. |  | QAT "MDC-F29B1E823FF24AD490BBFEE45079B809" "NC-PORTERK-068C3936ABD442EF84D1CF8999AD9E38"
ORIS 56249 (NCEMC Anson Plant) Location ES6-B | FF2LBAS | FF2B-Q32016-12A-22 |  | 12A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-F29B1E823FF24AD490BBFEE45079B809" "NC-PORTERK-068C3936ABD442EF84D1CF8999AD9E38"
ORIS 56249 (NCEMC Anson Plant) Location ES6-B | FF2LBAS | FF2B-Q32021-12A-22 |  | 12A (GAS) | CRIT1 | FF2LBAS-17-B | Fired | You defined an invalid BaselineFuelFlowToLoadRatio for this test. This value must be greater than zero and less than 20,000. |  | QAT "MDC-F29B1E823FF24AD490BBFEE45079B809" "NC-PORTERK-C2BA677FE85D4E89B017D1D0CEAD1809"
ORIS 56249 (NCEMC Anson Plant) Location ES6-B | FF2LBAS | FF2B-Q32021-12A-22 |  | 12A (GAS) | INFORM | FF2LBAS-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-F29B1E823FF24AD490BBFEE45079B809" "NC-PORTERK-C2BA677FE85D4E89B017D1D0CEAD1809"

## FF2LTST
Location | Test Type | Test Number | Test Date-Time | Sys/Comp Info | Severity | EASEY Result Code | Fired | EASEY Result | Notes | Command Line Parameters
ORIS 56249 (NCEMC Anson Plant) Location ES1-A | FF2LTST | FF2L-Q32021-01A-1 |  | 01A (CO2) | CRIT1 | FF2LTST-1-B | Fired | According to the monitoring system record, the monitoring system for this fuel flow-to-load test was not a fuel flow system. |  | QAT "MDC-F3ED630C7DE34EFA8BB22A34B636F88B" "NC-PORTERK-2C6905A0FC1245B8BC2358A8262E71F8"
ORIS 56249 (NCEMC Anson Plant) Location ES1-A | FF2LTST | FF2L-Q32021-01A-1 |  | 01A (CO2) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-F3ED630C7DE34EFA8BB22A34B636F88B" "NC-PORTERK-2C6905A0FC1245B8BC2358A8262E71F8"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q12019-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-11-A | Fired | You did not provide TestResultCode, which is required for this test. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-6D401A983DDA4D919F2B6EC67DB6E651"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q12019-02A-2 |  | 02A (GAS) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-6D401A983DDA4D919F2B6EC67DB6E651"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q12020-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-7-A | Fired | The value -1 in the field NumberOfHoursExcludedCofiring for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-0BAEAEC0BC024BF0B46489F9EB39D613"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q12020-02A-2 |  | 02A (GAS) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-0BAEAEC0BC024BF0B46489F9EB39D613"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q12021-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-5-E | Fired | The TestResultCode of the fuel flow-to-load test indicates a failing test, but the AverageDifference indicates a passing test. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-2E18521EDF874146996237F7184208FC"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q12021-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-6-C | Fired | The NumberOfHoursUsed was less than 168 which is the minimum required to complete the quarterly fuel flow-to-load test. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-2E18521EDF874146996237F7184208FC"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q12021-02A-2 |  | 02A (GAS) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-2E18521EDF874146996237F7184208FC"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q22019-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-10-A | Fired | You did not provide TestReasonCode, which is required for this test. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-D1D6E2A3226449298D5F78B51BC674EF"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q22019-02A-2 |  | 02A (GAS) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-D1D6E2A3226449298D5F78B51BC674EF"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q22020-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-4-B | Fired | The TestBasisCode is inconsistent with the data submitted in the associated fuel flow-to-load baseline data. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-E06718BEF23B45F7BB7163593FF55571"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q22020-02A-2 |  | 02A (GAS) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-E06718BEF23B45F7BB7163593FF55571"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q22021-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-3-A | Fired | You did not provide TestBasisCode, which is required for this test. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-9EBE9F31F97A40B4A550E6ADFC3BB93E"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q22021-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-6-C | Fired | The NumberOfHoursUsed was less than 168 which is the minimum required to complete the quarterly fuel flow-to-load test. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-9EBE9F31F97A40B4A550E6ADFC3BB93E"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q22021-02A-2 |  | 02A (GAS) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-9EBE9F31F97A40B4A550E6ADFC3BB93E"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q32019-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-9-A | Fired | The value -1 in the field NumberOfHoursExcludedLowRange for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-15CC64B2F83B450D88C2ED86BB1CD36C"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q32019-02A-2 |  | 02A (GAS) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-15CC64B2F83B450D88C2ED86BB1CD36C"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q32021-02A-2 |  | 02A (GAS) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-FDA53799F10F4AAFA43AF220712AFBF8"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q42018-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-12-A | Fired | The total number of hours used in the fuel flow-to-load or GHR analysis and the number of hours excluded exceed the total number of hours in the quarter. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-68AAAFBB42A1472BA590A2A55FB26855"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q42018-02A-2 |  | 02A (GAS) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-68AAAFBB42A1472BA590A2A55FB26855"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q42019-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-8-A | Fired | The value -1 in the field NumberOfHoursExcludedRamping for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-F106F030CEEF492EA479A9DEC6DB5028"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q42019-02A-2 |  | 02A (GAS) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-F106F030CEEF492EA479A9DEC6DB5028"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q42020-02A-2 |  | 02A (GAS) | CRIT1 | FF2LTST-6-A | Fired | The value -1 in the field NumberOfHoursUsed for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-A137227A737345E6BA99604C9FC5E3B8"
ORIS 56249 (NCEMC Anson Plant) Location ES1-B | FF2LTST | FF2L-Q42020-02A-2 |  | 02A (GAS) | INFORM | FF2LTST-2-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-9D275D287FBF42CAAECBECA1A097558D" "NC-PORTERK-A137227A737345E6BA99604C9FC5E3B8"

## LINE
Location | Test Type | Test Number | Test Date-Time | Sys/Comp Info | Severity | EASEY Result Code | Fired | EASEY Result | Notes
ORIS 3 (Barry) Location 5 | HGSI3 | 20160303122929CMM | 2016-03-03 16:28 | CMM (HG) | CRIT1 | LINEAR-29-F | Yes | You reported a TestResultCode of "PASSED", but the results recalculated or determined from the other reported values indicate that you should have reported "PASSAPS".
ORIS 3 (Barry) Location 5 | HGSI3 | 20160303122929CMM | 2016-03-03 16:28 | CMM (HG) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500CD1 | 2020-11-10 12:13 | CD1 (CO2) | CRIT1 | LINEAR-11-A | Yes | You reported that two or more reference gas injections were performed at the same date and time. Two injections in a linearity check cannot be performed simultaneously.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500CD1 | 2020-11-10 12:13 | CD1 (CO2) | CRIT1 | LINEAR-12-A | Yes | Two or more consecutive reference gas injections have the same calibration gas level. Section 6.2 in Appendix A of 40 CFR Part 75 requires successive gas injections during a linearity check to be at different calibration gas levels.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500CD1 | 2020-11-10 12:13 | CD1 (CO2) | CRIT1 | LINEAR-14-A | Yes | You have reported more than one linearity summary record for Calibration Gas Level HIGH.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500CD1 | 2020-11-10 12:13 | CD1 (CO2) | CRIT1 | LINEAR-26-C | Yes | The reported APSIndicator of 1 is inconsistent with the calculated APSIndicator of 0. An alternative performance specification is not required to pass Calibration Gas Level MID.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500CD1 | 2020-11-10 12:13 | CD1 (CO2) | CRIT1 | PGVP-7-A | Yes | You did not report Protocol Gas records for all three gas levels for all reference gases used in the test.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500CD1 | 2020-11-10 12:13 | CD1 (CO2) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500NX1 | 2020-11-10 12:13 | NX1 (NOX) | CRIT1 | LINEAR-6-A | Yes | You reported a Test End Date, Hour, and Minute that is not the same as the Injection Date, Hour, and Minute of the last injection in the test.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500NX1 | 2020-11-10 12:13 | NX1 (NOX) | CRIT1 | LINEAR-24-A | Yes | An injection in this test was conducted at the same time as an injection in another linearity check for the alternate range of the same analyzer.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500NX1 | 2020-11-10 12:13 | NX1 (NOX) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500SD1 | 2020-11-10 12:13 | SD1 (SO2) | CRIT1 | LINEAR-25-B | Yes | There were more than three gas injections reported for Calibration Gas Level LOW. Only report the three injections used for analysis at this Calibration Gas Level.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500SD1 | 2020-11-10 12:13 | SD1 (SO2) | CRIT1 | LINEAR-27-B | Yes | The Percent Error reported in the Linearity Summary record for Calibration Gas Level LOW is inconsistent with the value which has been recalculated from the injections associated with the test.
ORIS 3 (Barry) Location 5 | LINE | 20201110111500SD1 | 2020-11-10 12:13 | SD1 (SO2) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20201110130221NX1L | 2020-11-10 13:37 | NX1 (NOX) | CRIT1 | LINEAR-24-A | Yes | An injection in this test was conducted at the same time as an injection in another linearity check for the alternate range of the same analyzer.
ORIS 3 (Barry) Location 5 | LINE | 20201110130221NX1L | 2020-11-10 13:37 | NX1 (NOX) | CRIT1 | LINEAR-29-F | Yes | You reported a TestResultCode of "PASSED", but the results recalculated or determined from the other reported values indicate that you should have reported "PASSAPS".
ORIS 3 (Barry) Location 5 | LINE | 20201110130221NX1L | 2020-11-10 13:37 | NX1 (NOX) | CRIT1 | LINEAR-37-A | Yes | You did not provide APSIndicator, which is required for Calibration Gas Level HIGH.
ORIS 3 (Barry) Location 5 | LINE | 20201110130221NX1L | 2020-11-10 13:37 | NX1 (NOX) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210215114848NX1L | 2021-02-15 12:24 | NX1 (NOX) | CRIT1 | LINEAR-21-B | Yes | You reported the value -1.000, which is not in the list of valid values, in the field ReferenceValue for Injection for Gas Calibration Level LOW that was performed on 2/15/2021 11:46.
ORIS 3 (Barry) Location 5 | LINE | 20210215114848NX1L | 2021-02-15 12:24 | NX1 (NOX) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210215114848NX1L | 2021-02-15 12:24 | NX1 (NOX) | INFORM | LINEAR-26-A | Yes | The software could not evaluate the linearity check calculations reported for Calibration Gas Level LOW, because of the errors listed above.
ORIS 3 (Barry) Location 5 | LINE | 20210215114848SD1L | 2021-02-15 12:24 | SD1 (SO2) | CRIT1 | LINEAR-23-A | Yes | The reference values in this test are not consistent with the calibration gas levels. The reference values of low-level gas injections must be less than those of mid-level gas injections; and the reference values of mid-level gas injections must be less than those of high-level gas injections.
ORIS 3 (Barry) Location 5 | LINE | 20210215114848SD1L | 2021-02-15 12:24 | SD1 (SO2) | CRIT1 | LINEAR-27-B | Yes | The Percent Error reported in the Linearity Summary record for Calibration Gas Level LOW is inconsistent with the value which has been recalculated from the injections associated with the test.
ORIS 3 (Barry) Location 5 | LINE | 20210215114848SD1L | 2021-02-15 12:24 | SD1 (SO2) | CRIT2 | LINEAR-22-A | Yes | The tag value of the "LOW" level reference calibration gas for the injection data is 60.0% of span and does not meet the performance specifications of 40 CFR Part 75. The concentration of the low reference calibration gas must be between 20.0% and 30.0% of the span value. This test is invalid.
ORIS 3 (Barry) Location 5 | LINE | 20210215114848SD1L | 2021-02-15 12:24 | SD1 (SO2) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210215122903CD1 | 2021-02-15 13:20 | CD1 (CO2) | CRIT1 | LINEAR-27-B | Yes | The Percent Error reported in the Linearity Summary record for Calibration Gas Level MID is inconsistent with the value which has been recalculated from the injections associated with the test.
ORIS 3 (Barry) Location 5 | LINE | 20210215122903CD1 | 2021-02-15 13:20 | CD1 (CO2) | CRIT2 | LINEAR-22-C | Yes | The tag value of the "MID" level reference calibration gas for the injection data is 85.0% of span and does not meet the performance specifications of 40 CFR Part 75. The concentration of the mid reference calibration gas must be between 50.0% and 60.0% of the span value. This test is invalid.
ORIS 3 (Barry) Location 5 | LINE | 20210215122903CD1 | 2021-02-15 13:20 | CD1 (CO2) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210215122903NX1 | 2021-02-15 13:20 | NX1 (NOX) | CRIT1 | LINEAR-20-A | Yes | You did not provide MeasuredValue, which is required for Injection for Gas Calibration Level MID that was performed on 2/15/2021 12:49.
ORIS 3 (Barry) Location 5 | LINE | 20210215122903NX1 | 2021-02-15 13:20 | NX1 (NOX) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210215122903NX1 | 2021-02-15 13:20 | NX1 (NOX) | INFORM | LINEAR-26-A | Yes | The software could not evaluate the linearity check calculations reported for Calibration Gas Level MID, because of the errors listed above.
ORIS 3 (Barry) Location 5 | LINE | 20210215122903SD1 | 2021-02-15 13:20 | SD1 (SO2) | CRIT1 | LINEAR-19-A | Yes | The injection date, hour, and/or minute for Injection for Gas Calibration Level HIGH that was performed on 2/15/2021 24:45 is invalid.
ORIS 3 (Barry) Location 5 | LINE | 20210215122903SD1 | 2021-02-15 13:20 | SD1 (SO2) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210215122903SD1 | 2021-02-15 13:20 | SD1 (SO2) | INFORM | LINEAR-26-A | Yes | The software could not evaluate the linearity check calculations reported for Calibration Gas Level HIGH, because of the errors listed above.
ORIS 3 (Barry) Location 5 | LINE | 20210607133032NX1L | 2021-06-07 13:53 | NX1 (NOX) | CRIT1 | LINEAR-17-B | Yes | The value -1.000 in the field MeanReferenceValue for Calibration Gas Level MID is not within the range of valid values. This value must be greater than or equal to zero.
ORIS 3 (Barry) Location 5 | LINE | 20210607133032NX1L | 2021-06-07 13:53 | NX1 (NOX) | NONCRIT | LINEAR-27-C | Yes | The MeanReferenceValue reported in the Linearity Summary record for Calibration Gas Level MID is inconsistent with the value which has been recalculated from the injections associated with the test.
ORIS 3 (Barry) Location 5 | LINE | 20210607133032NX1L | 2021-06-07 13:53 | NX1 (NOX) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210607133032SD1L | 2021-06-07 13:53 | SD1 (SO2) | CRIT1 | LINEAR-18-A | Yes | You did not provide PercentError, which is required for Calibration Gas Level LOW.
ORIS 3 (Barry) Location 5 | LINE | 20210607133032SD1L | 2021-06-07 13:53 | SD1 (SO2) | CRIT1 | LINEAR-26-C | Yes | The reported APSIndicator of 1 is inconsistent with the calculated APSIndicator of 0. An alternative performance specification is not required to pass Calibration Gas Level MID.
ORIS 3 (Barry) Location 5 | LINE | 20210607133032SD1L | 2021-06-07 13:53 | SD1 (SO2) | CRIT1 | LINEAR-26-C | Yes | The reported APSIndicator of 1 is inconsistent with the calculated APSIndicator of 0. An alternative performance specification is not required to pass Calibration Gas Level HIGH.
ORIS 3 (Barry) Location 5 | LINE | 20210607133032SD1L | 2021-06-07 13:53 | SD1 (SO2) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210614135748CD1 | 2021-06-14 14:56 | CD1 (CO2) | CRIT1 | LINEAR-16-A | Yes | You did not provide MeanMeasuredValue, which is required for Calibration Gas Level HIGH.
ORIS 3 (Barry) Location 5 | LINE | 20210614135748CD1 | 2021-06-14 14:56 | CD1 (CO2) | CRIT1 | LINEAR-29-F | Yes | You reported a TestResultCode of "PASSED", but the results recalculated or determined from the other reported values indicate that you should have reported "PASSAPS".
ORIS 3 (Barry) Location 5 | LINE | 20210614135748CD1 | 2021-06-14 14:56 | CD1 (CO2) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210614135748NX1 | 2021-06-14 14:56 | NX1 (NOX) | CRIT1 | LINEAR-13-A | Yes | This linearity check was conducted at the same time as another linearity check for the same component and range.
ORIS 3 (Barry) Location 5 | LINE | 20210614135748NX1 | 2021-06-14 14:56 | NX1 (NOX) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210614135748SD1 | 2021-06-14 14:56 | SD1 (SO2) | CRIT1 | LINEAR-12-A | Yes | Two or more consecutive reference gas injections have the same calibration gas level. Section 6.2 in Appendix A of 40 CFR Part 75 requires successive gas injections during a linearity check to be at different calibration gas levels.
ORIS 3 (Barry) Location 5 | LINE | 20210614135748SD1 | 2021-06-14 14:56 | SD1 (SO2) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210907110209CD1 | 2021-09-07 11:56 | CD1 (CO2) | INFORM | LINEAR-3-A | Yes | The TestResultCode indicates that the test was aborted. Linearity Summary and Linearity Injection records for this test will not be evaluated. If the test was aborted for a reason not related to monitor performance, you should not report the test.
ORIS 3 (Barry) Location 5 | LINE | 20210907110209CD1 | 2021-09-07 11:56 | CD1 (CO2) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210907110209NX1 | 2021-09-07 11:56 | NX1 (NOX) | CRIT1 | LINEAR-5-A | Yes | You reported a Test Begin Date, Hour, and Minute that is not the same as the Injection Date, Hour, and Minute of the first injection in the test.
ORIS 3 (Barry) Location 5 | LINE | 20210907110209NX1 | 2021-09-07 11:56 | NX1 (NOX) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210907110209SD1 | 2021-09-07 11:56 | SD1 (SO2) | CRIT1 | LINEAR-9-A | Yes | You did not provide TestReasonCode, which is required for this test.
ORIS 3 (Barry) Location 5 | LINE | 20210907110209SD1 | 2021-09-07 11:56 | SD1 (SO2) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210914102637NX1L | 2021-09-14 12:24 | NX1 (NOX) | CRIT1 | LINEAR-6-A | Yes | You reported a Test End Date, Hour, and Minute that is not the same as the Injection Date, Hour, and Minute of the last injection in the test.
ORIS 3 (Barry) Location 5 | LINE | 20210914102637NX1L | 2021-09-14 12:24 | NX1 (NOX) | CRIT1 | LINEAR-26-C | Yes | The reported APSIndicator of 1 is inconsistent with the calculated APSIndicator of 0. An alternative performance specification is not required to pass Calibration Gas Level HIGH.
ORIS 3 (Barry) Location 5 | LINE | 20210914102637NX1L | 2021-09-14 12:24 | NX1 (NOX) | CRIT1 | LINEAR-26-C | Yes | The reported APSIndicator of 1 is inconsistent with the calculated APSIndicator of 0. An alternative performance specification is not required to pass Calibration Gas Level MID.
ORIS 3 (Barry) Location 5 | LINE | 20210914102637NX1L | 2021-09-14 12:24 | NX1 (NOX) | CRIT1 | LINEAR-26-C | Yes | The reported APSIndicator of 1 is inconsistent with the calculated APSIndicator of 0. An alternative performance specification is not required to pass Calibration Gas Level LOW.
ORIS 3 (Barry) Location 5 | LINE | 20210914102637NX1L | 2021-09-14 12:24 | NX1 (NOX) | CRIT1 | LINEAR-29-G | Yes | You reported a TestResultCode of "PASSAPS", but the results recalculated or determined from the other reported values indicate that you should have reported "PASSED".
ORIS 3 (Barry) Location 5 | LINE | 20210914102637NX1L | 2021-09-14 12:24 | NX1 (NOX) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | 20210914102637SD1L | 2021-09-14 11:24 | SD1 (SO2) | CRIT1 | LINEAR-5-A | Yes | You reported a Test Begin Date, Hour, and Minute that is not the same as the Injection Date, Hour, and Minute of the first injection in the test.
ORIS 3 (Barry) Location 5 | LINE | 20210914102637SD1L | 2021-09-14 11:24 | SD1 (SO2) | CRIT1 | LINEAR-11-A | Yes | You reported that two or more reference gas injections were performed at the same date and time. Two injections in a linearity check cannot be performed simultaneously.
ORIS 3 (Barry) Location 5 | LINE | 20210914102637SD1L | 2021-09-14 11:24 | SD1 (SO2) | CRIT1 | LINEAR-26-C | Yes | The reported APSIndicator of 1 is inconsistent with the calculated APSIndicator of 0. An alternative performance specification is not required to pass Calibration Gas Level MID.
ORIS 3 (Barry) Location 5 | LINE | 20210914102637SD1L | 2021-09-14 11:24 | SD1 (SO2) | INFORM | LINEAR-4-C | Yes | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval.
ORIS 3 (Barry) Location 5 | LINE | AAA | 2021-06-15 10:00 | NX1 (NOX) | CRIT1 | LINEAR-13-A | Yes | This linearity check was conducted at the same time as another linearity check for the same component and range.
ORIS 3 (Barry) Location 5 | LINE | AAA | 2021-06-15 10:00 | NX1 (NOX) | CRIT1 | LINEAR-28-A | Yes | You have reported fewer than three calibration gas levels in this test.
ORIS 3 (Barry) Location 5 | LINE | AAA | 2021-06-15 10:00 | NX1 (NOX) | CRIT1 | PGVP-7-B | Yes | You did not report any valid Protocol Gas records for this test. This information is required by the Protocol Gas Verification Program reporting rule.

## RATA
Location | Test Type | Test Number | Test Date-Time | Sys/Comp Info | Severity | EASEY Result Code | Fired | EASEY Result | Notes | Command Line Parameters
ORIS 3 (Barry) Location 4 | RATA | 201502051633ABD | 2015-02-05 17:27 | ABD (FLOW) | CRIT1 | RATA-58-D | Fired | You have provided a value for CalculatedWAF for Operating Level H, which is not appropriate for a test using this reference method. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-01E8551E36164190A40FBF7272B6F865"
ORIS 3 (Barry) Location 4 | RATA | 201502051633ABD | 2015-02-05 17:27 | ABD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-01E8551E36164190A40FBF7272B6F865"
ORIS 3 (Barry) Location 4 | RATA | 201503111616ABD | 2015-03-11 17:09 | ABD (FLOW) | CRIT1 | RATA-59-B | Fired | You have provided a value for DefaultWAF for Operating Level H, which is not appropriate for a test using this reference method. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-7AE1494EB29D4007B7B243DFA692097C"
ORIS 3 (Barry) Location 4 | RATA | 201503111616ABD | 2015-03-11 17:09 | ABD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-7AE1494EB29D4007B7B243DFA692097C"
ORIS 3 (Barry) Location 4 | RATA | 201603230709ABD | 2016-03-23 15:57 | ABD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-5458DF5CC5314F3AA177F4D7A84801FF"
ORIS 3 (Barry) Location 4 | RATA | 201603230709ABD | 2016-03-23 15:57 | ABD (FLOW) | INFORM | RATA-60-A | Fired | You have reported a ReferenceMethodCode for Operating Level H that does not indicate the use of a rectangular duct WAF, but you have reported a RectangularDuctWAF record for the location. If you use a rectangular duct WAF, you must report a reference method of 2J, 2FJ, or 2GJ. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-5458DF5CC5314F3AA177F4D7A84801FF"
ORIS 3 (Barry) Location 4 | RATA | 201603230709ABD | 2016-03-23 15:57 | ABD (FLOW) | INFORM | RATA-60-A | Fired | You have reported a ReferenceMethodCode for Operating Level L that does not indicate the use of a rectangular duct WAF, but you have reported a RectangularDuctWAF record for the location. If you use a rectangular duct WAF, you must report a reference method of 2J, 2FJ, or 2GJ. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-5458DF5CC5314F3AA177F4D7A84801FF"
ORIS 3 (Barry) Location 4 | RATA | 201703211826ABD | 2017-03-22 17:58 | ABD (FLOW) | CRIT1 | RATA-61-B | Fired | You have provided a value for NumberOfTraversePoints for Operating Level H, which is not appropriate for a test using this reference method. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-C879C11F36E84EA7B4F79FDBD872A33E"
ORIS 3 (Barry) Location 4 | RATA | 201703211826ABD | 2017-03-22 17:58 | ABD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-C879C11F36E84EA7B4F79FDBD872A33E"
ORIS 3 (Barry) Location 4 | RATA | 201803210644ABD | 2018-03-21 08:23 | ABD (FLOW) | CRIT1 | RATA-9-D | Fired | The sum of the percentages provided for Low, Mid and High load levels does not represent 100% of the range of operation. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-25573BDE735B4FADB71F73DD47B505CB"
ORIS 3 (Barry) Location 4 | RATA | 201803210644ABD | 2018-03-21 08:23 | ABD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-25573BDE735B4FADB71F73DD47B505CB"
ORIS 3 (Barry) Location 4 | RATA | 201803210644ABD | 2018-03-21 08:23 | ABD (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-25573BDE735B4FADB71F73DD47B505CB"
ORIS 3 (Barry) Location 4 | RATA | 201902271151ABD | 2019-02-27 13:16 | ABD (FLOW) | CRIT1 | RATA-9-D | Fired | The sum of the percentages provided for Low, Mid and High load levels does not represent 100% of the range of operation. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-88FB424CF2024BC6851C050E632F35FB"
ORIS 3 (Barry) Location 4 | RATA | 201902271151ABD | 2019-02-27 13:16 | ABD (FLOW) | CRIT1 | RATA-10-A | Fired | You did not provide MidLoadPercentage, which is required for Test Claim SLC. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-88FB424CF2024BC6851C050E632F35FB"
ORIS 3 (Barry) Location 4 | RATA | 201902271151ABD | 2019-02-27 13:16 | ABD (FLOW) | CRIT2 | RATA-38-A | Fired | The average gross unit load recalculated from the values in the run records for Operating Level L is not within the low level operating range defined in the load record. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-88FB424CF2024BC6851C050E632F35FB"
ORIS 3 (Barry) Location 4 | RATA | 201902271151ABD | 2019-02-27 13:16 | ABD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-88FB424CF2024BC6851C050E632F35FB"
ORIS 3 (Barry) Location 4 | RATA | 201902271151ABD | 2019-02-27 13:16 | ABD (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-88FB424CF2024BC6851C050E632F35FB"
ORIS 3 (Barry) Location 4 | RATA | 201902280821ABF | 2019-02-28 14:56 | ABF (HG) | CRIT1 | RATA-50-A | Fired | This RATA was conducted at the same time as another RATA for the same UnitStackID and MonitoringSystemID. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-193C63EEEC494CA7B102E00A77717319"
ORIS 3 (Barry) Location 4 | RATA | 201902280821ABF | 2019-02-28 14:56 | ABF (HG) | CRIT1 | RATA-51-B | Fired | The OverallBiasAdjustmentFactor for this test is not within the range of valid values. This value must be equal to or greater than 1.000. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-193C63EEEC494CA7B102E00A77717319"
ORIS 3 (Barry) Location 4 | RATA | 201902280821ABF | 2019-02-28 14:56 | ABF (HG) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-193C63EEEC494CA7B102E00A77717319"
ORIS 3 (Barry) Location 4 | RATA | 202004080728ABF | 2020-04-08 14:10 | ABF (HG) | CRIT1 | RATA-4-A | Fired | You did not provide TestReasonCode, which is required for this RATA. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-C3B09F361E9D45118938CF06A9FDAC7C"
ORIS 3 (Barry) Location 4 | RATA | 202004080728ABF | 2020-04-08 14:10 | ABF (HG) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-C3B09F361E9D45118938CF06A9FDAC7C"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABA | 2020-04-08 13:54 | ABA (SO2) | CRIT1 | RATA-5-A | Fired | The following runs had a begin and end time that overlapped another run in the RATA: Operating Level H Run Number 2. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-CD719F5C71004ED987EDD8F5A8DC3A2A"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABA | 2020-04-08 13:54 | ABA (SO2) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-CD719F5C71004ED987EDD8F5A8DC3A2A"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABA | 2020-04-08 13:54 | ABA (SO2) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-CD719F5C71004ED987EDD8F5A8DC3A2A"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABA | 2020-04-08 13:54 | ABA (SO2) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-CD719F5C71004ED987EDD8F5A8DC3A2A"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABB | 2020-04-08 13:54 | ABB (NOX) | CRIT1 | RATA-35-A | Fired | The values reported for RelativeAccuracy in the RATA summary record for Operating Level H are inconsistent with the values that have been recalculated from the run records. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-2D8FE24CE80244688914A1C95E4A980D"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABB | 2020-04-08 13:54 | ABB (NOX) | CRIT1 | RATA-48-C | Fired | The OverallRelativeAccuracy reported in the RATA record is not equal to the highest relative accuracy recalculated from the run records for each operating level. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-2D8FE24CE80244688914A1C95E4A980D"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABB | 2020-04-08 13:54 | ABB (NOX) | CRIT1 | RATA-53-D | Fired | The TestResultCode indicates a passing test, but the relative accuracy recalculated from the run records indicates a failing test. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-2D8FE24CE80244688914A1C95E4A980D"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABB | 2020-04-08 13:54 | ABB (NOX) | NONCRIT | RATA-6-A | Fired | For one or more runs of this RATA the value from the NOX system being tested is greater than the maximum emission rate defined in the NORX default record. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-2D8FE24CE80244688914A1C95E4A980D"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABB | 2020-04-08 13:54 | ABB (NOX) | NONCRIT | RATA-40-A | Fired | The values reported for MeanDifference and MeanCEMValue in the RATA summary record for Operating Level H are inconsistent with the values that have been recalculated from the run records. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-2D8FE24CE80244688914A1C95E4A980D"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABB | 2020-04-08 13:54 | ABB (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-2D8FE24CE80244688914A1C95E4A980D"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABB | 2020-04-08 13:54 | ABB (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-2D8FE24CE80244688914A1C95E4A980D"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABB | 2020-04-08 13:54 | ABB (NOX) | NONE | PGVP-14-A | Suppressed | You reported the same Cylinder Identifier for more than one protocol gas cylinder. | Suppressed in ECMPS 1.0 and ECMPS 2.0. | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-2D8FE24CE80244688914A1C95E4A980D"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABB | 2020-04-08 13:54 | ABB (NOX) | NONE | PGVP-14-A | Suppressed | You reported the same Cylinder Identifier for more than one protocol gas cylinder. | Suppressed in ECMPS 1.0 and ECMPS 2.0. | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-2D8FE24CE80244688914A1C95E4A980D"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABB | 2020-04-08 13:54 | ABB (NOX) | NONE | PGVP-14-A | Suppressed | You reported the same Cylinder Identifier for more than one protocol gas cylinder. | Suppressed in ECMPS 1.0 and ECMPS 2.0. | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-2D8FE24CE80244688914A1C95E4A980D"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABB | 2020-04-08 13:54 | ABB (NOX) | NONE | PGVP-14-A | Suppressed | You reported the same Cylinder Identifier for more than one protocol gas cylinder. | Suppressed in ECMPS 1.0 and ECMPS 2.0. | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-2D8FE24CE80244688914A1C95E4A980D"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABC | 2020-04-08 13:54 | ABC (CO2) | CRIT1 | RATA-8-C | Fired | The Test Claim ORE for this RATA is invalid, because this claim only applies to a FLOW monitoring system. |  | "QAT" "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-7901720C0BEF428F96A965E3624258F4"
ORIS 3 (Barry) Location 4 | RATA | 202004080834ABC | 2020-04-08 13:54 | ABC (CO2) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-7901720C0BEF428F96A965E3624258F4"
ORIS 3 (Barry) Location 4 | RATA | 202004090648ABD | 2020-04-09 10:29 | ABD (FLOW) | NONCRIT | RATA-7-A | Fired | For one or more runs of this flow RATA the CEM Value and/or Reference Value was not rounded to the nearest 1000 scfh. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-4AD7230E135142F9960D42E9FC6A55AA"
ORIS 3 (Barry) Location 4 | RATA | 202004090648ABD | 2020-04-09 10:29 | ABD (FLOW) | INFORM | RATA-27-C | Fired | You have reported more than 3 decimal places for CEMValue in Operating Level H Run Number 1, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-4AD7230E135142F9960D42E9FC6A55AA"
ORIS 3 (Barry) Location 4 | RATA | 202004090648ABD | 2020-04-09 10:29 | ABD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-4AD7230E135142F9960D42E9FC6A55AA"
ORIS 3 (Barry) Location 4 | RATA | 202004090648ABD | 2020-04-09 10:29 | ABD (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-4AD7230E135142F9960D42E9FC6A55AA"
ORIS 3 (Barry) Location 4 | RATA | 202004090648ABD | 2020-04-09 10:29 | ABD (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-4AD7230E135142F9960D42E9FC6A55AA"
ORIS 3 (Barry) Location 4 | RATA | 202004090648ABD | 2020-04-09 10:29 | ABD (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-4AD7230E135142F9960D42E9FC6A55AA"
ORIS 3 (Barry) Location 4 | RATA | 202107260542ABF | 2021-08-02 03:22 | ABF (HG) | CRIT1 | RATA-8-C | Fired | The Test Claim SLC for this RATA is invalid, because this claim only applies to a FLOW monitoring system. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-8FB13601DDC24D7081C8B72028566EA5"
ORIS 3 (Barry) Location 4 | RATA | 202107260542ABF | 2021-08-02 03:22 | ABF (HG) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-8FB13601DDC24D7081C8B72028566EA5"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABA | 2021-08-02 16:01 | ABA (SO2) | CRIT1 | RATA-18-B | Fired | You defined an invalid MeanRATAReferenceValue for Operating Level M. This value must be greater than zero and less than 20,000. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-8BBA59FEDD3444FF8EA22BEBA0358471"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABA | 2021-08-02 16:01 | ABA (SO2) | NONCRIT | RATA-40-A | Fired | The values reported for MeanRATAReferenceValue in the RATA summary record for Operating Level M are inconsistent with the values that have been recalculated from the run records. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-8BBA59FEDD3444FF8EA22BEBA0358471"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABA | 2021-08-02 16:01 | ABA (SO2) | NONCRIT | RATA-46-A | Fired | The test period for this RATA extended for more than 168 clock hours. This test may not meet the requirement that the test period for each single-load RATA be completed within 168 unit or stack operating hours. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-8BBA59FEDD3444FF8EA22BEBA0358471"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABA | 2021-08-02 16:01 | ABA (SO2) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-8BBA59FEDD3444FF8EA22BEBA0358471"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABA | 2021-08-02 16:01 | ABA (SO2) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-8BBA59FEDD3444FF8EA22BEBA0358471"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABB | 2021-08-02 16:01 | ABB (NOX) | CRIT1 | RATA-15-C | Fired | The OperatingLevelCode in the RATA Summary record should not be 'N'. Operating levels should be identified as 'N' only for peaking units or for stacks associated only with peaking units. |  | "QAT" "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-B2568D2520614D0D9FB1385A20E9D5F2"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABB | 2021-08-02 16:01 | ABB (NOX) | CRIT1 | RATA-16-E | Fired | You reported a reference method of "20" in the RATA Summary Data record for Operating Level N, but this method is no longer acceptable. |  | "QAT" "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-B2568D2520614D0D9FB1385A20E9D5F2"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABB | 2021-08-02 16:01 | ABB (NOX) | CRIT1 | RATA-34-B | Fired | The RATA for Operating Level N contains fewer than nine RATA run records with a run status of "RUNUSED". A minimum of nine runs are required for each complete operating level test. |  | "QAT" "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-B2568D2520614D0D9FB1385A20E9D5F2"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABB | 2021-08-02 16:01 | ABB (NOX) | NONCRIT | RATA-46-A | Fired | The test period for this RATA extended for more than 168 clock hours. This test may not meet the requirement that the test period for each single-load RATA be completed within 168 unit or stack operating hours. |  | "QAT" "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-B2568D2520614D0D9FB1385A20E9D5F2"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABB | 2021-08-02 16:01 | ABB (NOX) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level N, because of the errors listed above. |  | "QAT" "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-B2568D2520614D0D9FB1385A20E9D5F2"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABB | 2021-08-02 16:01 | ABB (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | "QAT" "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-B2568D2520614D0D9FB1385A20E9D5F2"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABB | 2021-08-02 16:01 | ABB (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | "QAT" "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-B2568D2520614D0D9FB1385A20E9D5F2"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABB | 2021-08-02 16:01 | ABB (NOX) | NONE | PGVP-14-A | Suppressed | You reported the same Cylinder Identifier for more than one protocol gas cylinder. | Suppressed in ECMPS 1.0 and ECMPS 2.0. | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-B2568D2520614D0D9FB1385A20E9D5F2"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABC | 2021-08-02 16:01 | ABC (CO2) | CRIT1 | RATA-17-A | Fired | You did not provide MeanCEMValue, which is required for Operating Level M. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-46AEB16D38C24BA1B87B8DE72E8C867F"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABC | 2021-08-02 16:01 | ABC (CO2) | NONCRIT | RATA-46-A | Fired | The test period for this RATA extended for more than 168 clock hours. This test may not meet the requirement that the test period for each single-load RATA be completed within 168 unit or stack operating hours. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-46AEB16D38C24BA1B87B8DE72E8C867F"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABC | 2021-08-02 16:01 | ABC (CO2) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-46AEB16D38C24BA1B87B8DE72E8C867F"
ORIS 3 (Barry) Location 4 | RATA | 202107260833ABC | 2021-08-02 16:01 | ABC (CO2) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-46AEB16D38C24BA1B87B8DE72E8C867F"
ORIS 3 (Barry) Location 4 | RATA | 202108021047ABD | 2021-08-02 14:41 | ABD (FLOW) | CRIT1 | RATA-19-A | Fired | You did not provide MeanDifference, which is required for Operating Level L. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-6FE6D291B924436D893BD8D3640C75C6"
ORIS 3 (Barry) Location 4 | RATA | 202108021047ABD | 2021-08-02 14:41 | ABD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-6FE6D291B924436D893BD8D3640C75C6"
ORIS 3 (Barry) Location 4 | RATA | 202108021047ABD | 2021-08-02 14:41 | ABD (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-6FE6D291B924436D893BD8D3640C75C6"
ORIS 3 (Barry) Location 4 | RATA | 202108021047ABD | 2021-08-02 14:41 | ABD (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "TWCORNEL5-6FE6D291B924436D893BD8D3640C75C6"
ORIS 3 (Barry) Location 4 | RATA | AAA | 2019-02-28 16:50 | ABF (HG) | CRIT1 | RATA-41-A | Fired | You did not report any operating level data for this test. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "CHV-LGIANN-539ABFCDE3464374B7D6D86A8A512708"
ORIS 3 (Barry) Location 4 | RATA | AAA | 2019-02-28 16:50 | ABF (HG) | CRIT1 | RATA-50-A | Fired | This RATA was conducted at the same time as another RATA for the same UnitStackID and MonitoringSystemID. |  | QAT "TWCORNEL5-F4E3DAADF24B4E1C8F2BEDD2DE59B436" "CHV-LGIANN-539ABFCDE3464374B7D6D86A8A512708"
ORIS 3 (Barry) Location 5 | RATA | 200905050746AD4 | 2009-05-05 11:00 | AD4 (FLOW) | CRIT1 | RATA-43-A | Fired | According to the run records of this RATA, the average gross unit load of Operating Level M is greater than or equal to the average gross unit load of Operating Level H. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-EC75979FD4B54BC0A87219490AE6F71C"
ORIS 3 (Barry) Location 5 | RATA | 200905050746AD4 | 2009-05-05 11:00 | AD4 (FLOW) | CRIT1 | TEST-22-B | Fired | A Monitoring Plan associated with this test has not been evaluated. You must evaluate all active and future Monitoring Plans containing the location in this test in order to complete the evaluation of this test. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-EC75979FD4B54BC0A87219490AE6F71C"
ORIS 3 (Barry) Location 5 | RATA | 200905050746AD4 | 2009-05-05 11:00 | AD4 (FLOW) | CRIT2 | RATA-38-B | Fired | The average gross unit load recalculated from the values in the run records for Operating Level M is not within the mid level operating range defined in the load record. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-EC75979FD4B54BC0A87219490AE6F71C"
ORIS 3 (Barry) Location 5 | RATA | 200905050746AD4 | 2009-05-05 11:00 | AD4 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-EC75979FD4B54BC0A87219490AE6F71C"
ORIS 3 (Barry) Location 5 | RATA | 201503250954ADD | 2015-03-25 12:12 | ADD (FLOW) | CRIT1 | RATA-42-A | Fired | According to the run records of this RATA, the average gross unit load of Operating Level L is greater than or equal to the average gross unit load of Operating Level M. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-A0FE7899A6EC4F63AB3ABFE54A336828"
ORIS 3 (Barry) Location 5 | RATA | 201503250954ADD | 2015-03-25 12:12 | ADD (FLOW) | CRIT2 | RATA-38-A | Fired | The average gross unit load recalculated from the values in the run records for Operating Level L is not within the low level operating range defined in the load record. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-A0FE7899A6EC4F63AB3ABFE54A336828"
ORIS 3 (Barry) Location 5 | RATA | 201503250954ADD | 2015-03-25 12:12 | ADD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-A0FE7899A6EC4F63AB3ABFE54A336828"
ORIS 3 (Barry) Location 5 | RATA | 201503250954ADD | 2015-03-25 12:12 | ADD (FLOW) | INFORM | RATA-60-A | Fired | You have reported a ReferenceMethodCode for Operating Level H that does not indicate the use of a rectangular duct WAF, but you have reported a RectangularDuctWAF record for the location. If you use a rectangular duct WAF, you must report a reference method of 2J, 2FJ, or 2GJ. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-A0FE7899A6EC4F63AB3ABFE54A336828"
ORIS 3 (Barry) Location 5 | RATA | 201503250954ADD | 2015-03-25 12:12 | ADD (FLOW) | INFORM | RATA-60-A | Fired | You have reported a ReferenceMethodCode for Operating Level L that does not indicate the use of a rectangular duct WAF, but you have reported a RectangularDuctWAF record for the location. If you use a rectangular duct WAF, you must report a reference method of 2J, 2FJ, or 2GJ. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-A0FE7899A6EC4F63AB3ABFE54A336828"
ORIS 3 (Barry) Location 5 | RATA | 201503250954ADD | 2015-03-25 12:12 | ADD (FLOW) | INFORM | RATA-60-A | Fired | You have reported a ReferenceMethodCode for Operating Level M that does not indicate the use of a rectangular duct WAF, but you have reported a RectangularDuctWAF record for the location. If you use a rectangular duct WAF, you must report a reference method of 2J, 2FJ, or 2GJ. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-A0FE7899A6EC4F63AB3ABFE54A336828"
ORIS 3 (Barry) Location 5 | RATA | 201902211047ADD | 2019-02-21 11:36 | ADD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-325BD5C2D2024566A9F6BCE34F92BEEC"
ORIS 3 (Barry) Location 5 | RATA | 201902211047ADD | 2019-02-21 11:36 | ADD (FLOW) | INFORM | RATA-60-A | Fired | You have reported a ReferenceMethodCode for Operating Level H that does not indicate the use of a rectangular duct WAF, but you have reported a RectangularDuctWAF record for the location. If you use a rectangular duct WAF, you must report a reference method of 2J, 2FJ, or 2GJ. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-325BD5C2D2024566A9F6BCE34F92BEEC"
ORIS 3 (Barry) Location 5 | RATA | 201902211047ADD | 2019-02-21 11:36 | ADD (FLOW) | INFORM | RATA-60-A | Fired | You have reported a ReferenceMethodCode for Operating Level L that does not indicate the use of a rectangular duct WAF, but you have reported a RectangularDuctWAF record for the location. If you use a rectangular duct WAF, you must report a reference method of 2J, 2FJ, or 2GJ. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-325BD5C2D2024566A9F6BCE34F92BEEC"
ORIS 3 (Barry) Location 5 | RATA | 201903130722ADE | 2019-03-13 14:41 | ADE (HG) | CRIT1 | RATA-44-A | Fired | You reported a test Begin Date, Hour, and Minute that is not the same as the BeginDate, BeginHour, and BeginMinute of the first run in the RATA. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-28CD8C6FB7D2420890EAA9D24882A265"
ORIS 3 (Barry) Location 5 | RATA | 201903130722ADE | 2019-03-13 14:41 | ADE (HG) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-28CD8C6FB7D2420890EAA9D24882A265"
ORIS 3 (Barry) Location 5 | RATA | 202003300811ADA | 2020-03-30 13:53 | ADA (SO2) | CRIT1 | RATA-20-A | Fired | You did not provide StandardDeviationDifference, which is required for Operating Level M. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-996D98021FBA480A828DB5B12D5414AC"
ORIS 3 (Barry) Location 5 | RATA | 202003300811ADA | 2020-03-30 13:53 | ADA (SO2) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-996D98021FBA480A828DB5B12D5414AC"
ORIS 3 (Barry) Location 5 | RATA | 202003300811ADA | 2020-03-30 13:53 | ADA (SO2) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, and MeanRATAReferenceValue, which is not permitted by Part 75. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-996D98021FBA480A828DB5B12D5414AC"
ORIS 3 (Barry) Location 5 | RATA | 202003300811ADB | 2020-03-30 13:53 | ADB (NOX) | CRIT1 | RATA-22-A | Fired | You have not reported the required value in the field TValue for Operating Level M. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-433CBCD6302542C38136488B847E5B0F"
ORIS 3 (Barry) Location 5 | RATA | 202003300811ADB | 2020-03-30 13:53 | ADB (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-433CBCD6302542C38136488B847E5B0F"
ORIS 3 (Barry) Location 5 | RATA | 202003300811ADB | 2020-03-30 13:53 | ADB (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-433CBCD6302542C38136488B847E5B0F"
ORIS 3 (Barry) Location 5 | RATA | 202003300811ADC | 2020-03-30 13:53 | ADC (CO2) | CRIT1 | RATA-21-A | Fired | You did not provide ConfidenceCoefficient, which is required for Operating Level M. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-7C7FCB5644714A6EB8F667D933D18B00"
ORIS 3 (Barry) Location 5 | RATA | 202003300811ADC | 2020-03-30 13:53 | ADC (CO2) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-7C7FCB5644714A6EB8F667D933D18B00"
ORIS 3 (Barry) Location 5 | RATA | 202003301130ADE | 2020-03-30 17:48 | ADE (HG) | CRIT1 | RATA-23-B | Fired | You defined an invalid AverageGrossUnitLoad for Operating Level M. This value must be greater than zero and less than 20,000. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-ECF52E6C3FCA4988ABBD8162EBE5B455"
ORIS 3 (Barry) Location 5 | RATA | 202003301130ADE | 2020-03-30 17:48 | ADE (HG) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-ECF52E6C3FCA4988ABBD8162EBE5B455"
ORIS 3 (Barry) Location 5 | RATA | 202003310710ADD | 2020-03-31 10:50 | ADD (FLOW) | CRIT1 | RATA-24-A | Fired | You did not provide RelativeAccuracy, which is required for Operating Level H. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-8C9CC7C2C99F4AE9B1EF6EF50BD6F5CD"
ORIS 3 (Barry) Location 5 | RATA | 202003310710ADD | 2020-03-31 10:50 | ADD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-8C9CC7C2C99F4AE9B1EF6EF50BD6F5CD"
ORIS 3 (Barry) Location 5 | RATA | 202003310710ADD | 2020-03-31 10:50 | ADD (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-8C9CC7C2C99F4AE9B1EF6EF50BD6F5CD"
ORIS 3 (Barry) Location 5 | RATA | 202003310710ADD | 2020-03-31 10:50 | ADD (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-8C9CC7C2C99F4AE9B1EF6EF50BD6F5CD"
ORIS 3 (Barry) Location 5 | RATA | 202102230833ADE | 2021-02-23 16:17 | ADE (HG) | CRIT1 | RATA-31-B | Fired | The run End Time is earlier than the run Begin Time for Operating Level M Run Number 10. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-B00664309D1B44BFBF4C820E0E017BBB"
ORIS 3 (Barry) Location 5 | RATA | 202102230833ADE | 2021-02-23 16:17 | ADE (HG) | CRIT1 | RATA-45-A | Fired | You reported a test EndDate, Hour, and Minute that is not the same as the EndDate, Hour, and Minute of the last run in the RATA test. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-B00664309D1B44BFBF4C820E0E017BBB"
ORIS 3 (Barry) Location 5 | RATA | 202102230833ADE | 2021-02-23 16:17 | ADE (HG) | CRIT2 | RATA-32-C | Fired | The run for Operating Level M Run Number 10 was less than 30 minutes. Each run must be at least 30 minutes in duration. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-B00664309D1B44BFBF4C820E0E017BBB"
ORIS 3 (Barry) Location 5 | RATA | 202102230833ADE | 2021-02-23 16:17 | ADE (HG) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level M, because of the errors listed above. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-B00664309D1B44BFBF4C820E0E017BBB"
ORIS 3 (Barry) Location 5 | RATA | 202102230833ADE | 2021-02-23 16:17 | ADE (HG) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-B00664309D1B44BFBF4C820E0E017BBB"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADA | 2021-02-23 14:38 | ADA (SO2) | CRIT1 | RATA-29-A | Fired | You did not provide RunStatusCode, which is required for Operating Level M Run Number 9. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-9DA309122FDF43AEA058A20FC97F2711"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADA | 2021-02-23 14:38 | ADA (SO2) | CRIT1 | RATA-34-B | Fired | The RATA for Operating Level M contains fewer than nine RATA run records with a run status of "RUNUSED". A minimum of nine runs are required for each complete operating level test. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-9DA309122FDF43AEA058A20FC97F2711"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADA | 2021-02-23 14:38 | ADA (SO2) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level M, because of the errors listed above. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-9DA309122FDF43AEA058A20FC97F2711"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADA | 2021-02-23 14:38 | ADA (SO2) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-9DA309122FDF43AEA058A20FC97F2711"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADA | 2021-02-23 14:38 | ADA (SO2) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-9DA309122FDF43AEA058A20FC97F2711"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADB | 2021-02-23 14:38 | ADB (NOX) | CRIT1 | RATA-30-A | Fired | The BeginDate, BeginHour, and/or BeginMinute for Operating Level M Run Number 9 is invalid. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-5E34C85AA97D46498159DCC7F42B6177"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADB | 2021-02-23 14:38 | ADB (NOX) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level M, because of the errors listed above. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-5E34C85AA97D46498159DCC7F42B6177"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADB | 2021-02-23 14:38 | ADB (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-5E34C85AA97D46498159DCC7F42B6177"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADB | 2021-02-23 14:38 | ADB (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-5E34C85AA97D46498159DCC7F42B6177"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADC | 2021-02-23 14:38 | ADC (CO2) | CRIT1 | RATA-26-A | Fired | You did not provide GrossUnitLoad, which is required for Operating Level M Run Number 9. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-F352A0528C9B4F539DA1EA43626F737B"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADC | 2021-02-23 14:38 | ADC (CO2) | CRIT2 | RATA-38-B | Fired | The average gross unit load recalculated from the values in the run records for Operating Level M is not within the mid level operating range defined in the load record. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-F352A0528C9B4F539DA1EA43626F737B"
ORIS 3 (Barry) Location 5 | RATA | 202102230957ADC | 2021-02-23 14:38 | ADC (CO2) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-F352A0528C9B4F539DA1EA43626F737B"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level L Run Number 7. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level L Run Number 1. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level L Run Number 2. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level L Run Number 3. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level L Run Number 4. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level L Run Number 5. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level L Run Number 6. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level L Run Number 9. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level L Run Number 8. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-55-A | Fired | You did not provide CO2OrO2ReferenceMethodCode, which is required for Operating Level L. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-56-A | Fired | You did not provide StackDiameter, which is required for Operating Level L. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | CRIT1 | RATA-57-A | Fired | You did not provide StackArea, which is required for Operating Level L. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level L, because of the errors listed above. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 5 | RATA | 202102240736ADD | 2021-02-24 08:26 | ADD (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-488E42008B434177BC7D7BFF138D18EF" "TWCORNEL5-E65B7C804F614A32AFD8E89D24BEE78A"
ORIS 3 (Barry) Location 6A | RATA | 201905150756MA3 | 2019-05-15 12:37 | MA3 (NOX) | NONCRIT | RATA-52-D | Fired | You reported a RATAFrequencyCode that is different from the value which was calculated from the runs of the RATA. |  | QAT "MDC-68FF9CD5F0C2464E85FD2A3C15D5A670" "TWCORNEL5-202CEDDEC3EE4E0CB580A4292411C237"
ORIS 3 (Barry) Location 6A | RATA | 201905150756MA3 | 2019-05-15 12:37 | MA3 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-68FF9CD5F0C2464E85FD2A3C15D5A670" "TWCORNEL5-202CEDDEC3EE4E0CB580A4292411C237"
ORIS 3 (Barry) Location 6A | RATA | 201905150756MA3 | 2019-05-15 12:37 | MA3 (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "MDC-68FF9CD5F0C2464E85FD2A3C15D5A670" "TWCORNEL5-202CEDDEC3EE4E0CB580A4292411C237"
ORIS 3 (Barry) Location 6A | RATA | 202001070829MA3 | 2020-01-07 12:48 | MA3 (NOX) | CRIT1 | RATA-33-A | Fired | You did not provide RATAReferenceValue, which is required for Operating Level H Run Number 9. |  | QAT "MDC-68FF9CD5F0C2464E85FD2A3C15D5A670" "TWCORNEL5-DFE02CAA396F4945B5E4FC2A400F83DE"
ORIS 3 (Barry) Location 6A | RATA | 202001070829MA3 | 2020-01-07 12:48 | MA3 (NOX) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "MDC-68FF9CD5F0C2464E85FD2A3C15D5A670" "TWCORNEL5-DFE02CAA396F4945B5E4FC2A400F83DE"
ORIS 3 (Barry) Location 6A | RATA | 202001070829MA3 | 2020-01-07 12:48 | MA3 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-68FF9CD5F0C2464E85FD2A3C15D5A670" "TWCORNEL5-DFE02CAA396F4945B5E4FC2A400F83DE"
ORIS 3 (Barry) Location 6A | RATA | 202001070829MA3 | 2020-01-07 12:48 | MA3 (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "MDC-68FF9CD5F0C2464E85FD2A3C15D5A670" "TWCORNEL5-DFE02CAA396F4945B5E4FC2A400F83DE"
ORIS 3 (Barry) Location 6A | RATA | 202103021150MA3 | 2021-03-02 16:05 | MA3 (NOX) | NONCRIT | RATA-36-A | Fired | The RATA summary record for Operating Level H contains an average gross unit load which is inconsistent with the average gross unit load recalculated from the run records used in the calculation of results. |  | QAT "MDC-68FF9CD5F0C2464E85FD2A3C15D5A670" "TWCORNEL5-65EFA8C0A2DC477785D8F48BF07A3BDF"
ORIS 3 (Barry) Location 6A | RATA | 202103021150MA3 | 2021-03-02 16:05 | MA3 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-68FF9CD5F0C2464E85FD2A3C15D5A670" "TWCORNEL5-65EFA8C0A2DC477785D8F48BF07A3BDF"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Gas Level LOW Gas Type ZERO. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Cylinder Identifier CC365215. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Cylinder Identifier CC410861. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Cylinder Identifier CC448536. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Cylinder Identifier EB0034740. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Gas Level LOW Gas Type ZERO. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-16-C | Fired | The ReferenceMethodCode 2F in the RATA Summary Data record for Operating Level H is not appropriate for a RATA conducted for a NOX system. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level H Run Number 3. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level H Run Number 4. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level H Run Number 5. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level H Run Number 6. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level H Run Number 7. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level H Run Number 8. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level H Run Number 9. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level H Run Number 1. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-28-C | Fired | You did not report a Flow Run record for Operating Level H Run Number 2. When a RATA is performed using method 2F or 2G, Flow Run record must be reported for each run used in the relative accuracy calculation. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-55-A | Fired | You did not provide CO2OrO2ReferenceMethodCode, which is required for Operating Level H. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-56-A | Fired | You did not provide StackDiameter, which is required for Operating Level H. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | CRIT1 | RATA-57-A | Fired | You did not provide StackArea, which is required for Operating Level H. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 201905160654MB3 | 2019-05-16 11:25 | MB3 (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-32CF0B122BD34482BAF98AC71CA959F2"
ORIS 3 (Barry) Location 6B | RATA | 202001080800MB3 | 2020-01-08 12:20 | MB3 (NOX) | CRIT1 | RATA-37-D | Fired | For Operating Level H you reported an APS flag of "1" even though the test passed without using the alternative performance specification. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-0084935B2BB8499EBCD9C9886E6D5E47"
ORIS 3 (Barry) Location 6B | RATA | 202001080800MB3 | 2020-01-08 12:20 | MB3 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-0084935B2BB8499EBCD9C9886E6D5E47"
ORIS 3 (Barry) Location 6B | RATA | 202001080800MB3 | 2020-01-08 12:20 | MB3 (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-0084935B2BB8499EBCD9C9886E6D5E47"
ORIS 3 (Barry) Location 6B | RATA | 202103031217MB3 | 2021-03-03 16:30 | MB3 (NOX) | CRIT1 | RATA-39-B | Fired | The BiasAdjustmentFactor for Operating Level H is not within the range of valid values. This value must be equal to or greater than 1.000. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-88A35594B2BD42F08BA2FFA0AE734792"
ORIS 3 (Barry) Location 6B | RATA | 202103031217MB3 | 2021-03-03 16:30 | MB3 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-88A35594B2BD42F08BA2FFA0AE734792"
ORIS 3 (Barry) Location 6B | RATA | 202103031217MB3 | 2021-03-03 16:30 | MB3 (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "MDC-A89416B9A1414C1CADE050800574A24C" "TWCORNEL5-88A35594B2BD42F08BA2FFA0AE734792"
ORIS 3 (Barry) Location 7A | RATA | 202002110910MC3 | 2020-02-11 13:50 | MC3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Gas Level LOW Gas Type ZERO. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-78E54EA179FA4C12B3640D3EA96110EC" "TWCORNEL5-4920D29CD9994B6A949889A8596C33CB"
ORIS 3 (Barry) Location 7A | RATA | 202002110910MC3 | 2020-02-11 13:50 | MC3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Gas Level LOW Gas Type ZERO. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-78E54EA179FA4C12B3640D3EA96110EC" "TWCORNEL5-4920D29CD9994B6A949889A8596C33CB"
ORIS 3 (Barry) Location 7A | RATA | 202002110910MC3 | 2020-02-11 13:50 | MC3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Cylinder Identifier CC456156. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-78E54EA179FA4C12B3640D3EA96110EC" "TWCORNEL5-4920D29CD9994B6A949889A8596C33CB"
ORIS 3 (Barry) Location 7A | RATA | 202002110910MC3 | 2020-02-11 13:50 | MC3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Cylinder Identifier CC708012. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-78E54EA179FA4C12B3640D3EA96110EC" "TWCORNEL5-4920D29CD9994B6A949889A8596C33CB"
ORIS 3 (Barry) Location 7A | RATA | 202002110910MC3 | 2020-02-11 13:50 | MC3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Cylinder Identifier EB0111514. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-78E54EA179FA4C12B3640D3EA96110EC" "TWCORNEL5-4920D29CD9994B6A949889A8596C33CB"
ORIS 3 (Barry) Location 7A | RATA | 202002110910MC3 | 2020-02-11 13:50 | MC3 (NOX) | CRIT1 | PGVP-6-B | Fired | You incorrectly reported a Protocol Gas Record for Cylinder Identifier XC007994B. You should only report a Protocol Gas record for a RATA performed using instrumental reference methods 3A, 6C, or 7E. |  | QAT "MDC-78E54EA179FA4C12B3640D3EA96110EC" "TWCORNEL5-4920D29CD9994B6A949889A8596C33CB"
ORIS 3 (Barry) Location 7A | RATA | 202002110910MC3 | 2020-02-11 13:50 | MC3 (NOX) | CRIT1 | RATA-41-A | Fired | You did not report any operating level data for this test. |  | QAT "MDC-78E54EA179FA4C12B3640D3EA96110EC" "TWCORNEL5-4920D29CD9994B6A949889A8596C33CB"
ORIS 3 (Barry) Location 7A | RATA | 202002110910MC3 | 2020-02-11 13:50 | MC3 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-78E54EA179FA4C12B3640D3EA96110EC" "TWCORNEL5-4920D29CD9994B6A949889A8596C33CB"
ORIS 3 (Barry) Location 7A | RATA | 202103090816MC3 | 2021-03-09 12:28 | MC3 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-78E54EA179FA4C12B3640D3EA96110EC" "TWCORNEL5-9B80321C2D124C4A97756A7B5F9A3D5A"
ORIS 3 (Barry) Location 7B | RATA | 202002120926MD3 | 2020-02-12 13:34 | MD3 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-ABF4B69D22C04494A78DA1667DFE9DE6" "TWCORNEL5-65025C1620A14A689818416E7BC229B6"
ORIS 3 (Barry) Location 7B | RATA | 202002120926MD3 | 2020-02-12 13:34 | MD3 (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "MDC-ABF4B69D22C04494A78DA1667DFE9DE6" "TWCORNEL5-65025C1620A14A689818416E7BC229B6"
ORIS 3 (Barry) Location 7B | RATA | 202103100709MD3 | 2021-03-10 12:23 | MD3 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-ABF4B69D22C04494A78DA1667DFE9DE6" "TWCORNEL5-31D8390EC76D497FBE78604622849B62"
ORIS 3 (Barry) Location 7B | RATA | 202103100709MD3 | 2021-03-10 12:23 | MD3 (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "MDC-ABF4B69D22C04494A78DA1667DFE9DE6" "TWCORNEL5-31D8390EC76D497FBE78604622849B62"
ORIS 3 (Barry) Location CS0AAN | RATA | 201407011200AA4 | 2014-07-01 15:42 | AA4 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-C0E3879920A14159BAA98E03F1980A7A" "TWCORNEL5-55787401DAE74BB4A1955DA7F70645B1"
ORIS 3 (Barry) Location CS0AAN | RATA | 201503181442AA4 | 2015-03-18 16:33 | AA4 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-C0E3879920A14159BAA98E03F1980A7A" "TWCORNEL5-5513A43028914335AD9AA4270AE1BF84"
ORIS 3 (Barry) Location CS0AAN | RATA | 201607250910AA4 | 2016-07-25 16:50 | AA4 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-C0E3879920A14159BAA98E03F1980A7A" "TWCORNEL5-5EB4F884D05640B4B50716170356CA4A"
ORIS 3 (Barry) Location CS0AAN | RATA | 201907150818AA2 | 2019-07-15 13:24 | AA2 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-C0E3879920A14159BAA98E03F1980A7A" "TWCORNEL5-E978B9C8FEE841FFB143162F917CCEF5"
ORIS 3 (Barry) Location CS0AAN | RATA | 201907150818AA2 | 2019-07-15 13:24 | AA2 (NOX) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-C0E3879920A14159BAA98E03F1980A7A" "TWCORNEL5-E978B9C8FEE841FFB143162F917CCEF5"
ORIS 3 (Barry) Location CS0AAN | RATA | 202001290814AA2 | 2020-01-29 12:36 | AA2 (NOX) | INFORM | RATA-3-A | Fired | The TestResultCode indicates that the test was aborted. RATA Summary, RATA Run, and RATA Traverse records for this test will not be evaluated. If the test was aborted for a reason not related to monitor performance, you should not report the test. |  | QAT "TWCORNEL5-C0E3879920A14159BAA98E03F1980A7A" "TWCORNEL5-D282130A5C71448194FB5D2B45CEA22F"
ORIS 3 (Barry) Location CS0AAN | RATA | 202001290814AA2 | 2020-01-29 12:36 | AA2 (NOX) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-C0E3879920A14159BAA98E03F1980A7A" "TWCORNEL5-D282130A5C71448194FB5D2B45CEA22F"
ORIS 3 (Barry) Location MS4A | RATA | 201403251415AB4 | 2014-03-25 15:13 | AB4 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BFCBF3162FE24E66BEB57E81A2938527" "TWCORNEL5-4551C052F3854D82822552A53AA692CC"
ORIS 3 (Barry) Location MS4A | RATA | 201407070911AB4 | 2014-07-07 10:18 | AB4 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BFCBF3162FE24E66BEB57E81A2938527" "TWCORNEL5-9056660D063F43A9AC0A4FF835ECBFB1"
ORIS 3 (Barry) Location MS4B | RATA | 201403251556ABJ | 2014-03-25 17:03 | ABJ (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BFCBF3162FE24E66BEB57E81A2938527" "TWCORNEL5-2608634F6A634D7E87D8555655EC490C"
ORIS 3 (Barry) Location MS5C | RATA | 201401161017AD9 | 2014-02-19 11:27 | AD9 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-A492BBDF51264399A9CFE4B73DF6A32C"
ORIS 3 (Barry) Location MS5C | RATA | 201503250954AD9 | 2015-03-25 12:12 | AD9 (FLOW) | CRIT1 | RATA-51-C | Fired | The reported OverallBiasAdjustmentFactor is inconsistent with the BAF recalculated by EPA. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-6F383AAACBCB4552A6F246A0F1D1AFFB"
ORIS 3 (Barry) Location MS5C | RATA | 201503250954AD9 | 2015-03-25 12:12 | AD9 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-6F383AAACBCB4552A6F246A0F1D1AFFB"
ORIS 3 (Barry) Location MS5C | RATA | 201512010831AD9 | 2015-12-01 11:47 | AD9 (FLOW) | CRIT1 | RATA-47-C | Fired | You did not perform the test for one or both of the operating levels that were designated as normal in the active load record. The correct BAF cannot be determined for this multi-load flow test. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-125D5F6A789A43B4A127F1CF0A90DDEE"
ORIS 3 (Barry) Location MS5C | RATA | 201512010831AD9 | 2015-12-01 11:47 | AD9 (FLOW) | CRIT1 | RATA-51-C | Fired | The reported OverallBiasAdjustmentFactor is inconsistent with the BAF recalculated by EPA. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-125D5F6A789A43B4A127F1CF0A90DDEE"
ORIS 3 (Barry) Location MS5C | RATA | 201512010831AD9 | 2015-12-01 11:47 | AD9 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-125D5F6A789A43B4A127F1CF0A90DDEE"
ORIS 3 (Barry) Location MS5C | RATA | 201603171132AD9 | 2016-03-17 12:26 | AD9 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-B855FD8066614583AA9AD2E45C76877F"
ORIS 3 (Barry) Location MS5C | RATA | 201702161345AD9 | 2017-02-16 14:29 | AD9 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-C48BD5B2C6F343AAAA7149DEB7AE0234"
ORIS 3 (Barry) Location MS5C | RATA | 201702161345AD9 | 2017-02-16 14:29 | AD9 (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-C48BD5B2C6F343AAAA7149DEB7AE0234"
ORIS 3 (Barry) Location MS5C | RATA | 201702161345AD9 | 2017-02-16 14:29 | AD9 (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-C48BD5B2C6F343AAAA7149DEB7AE0234"
ORIS 3 (Barry) Location MS5C | RATA | 201802201805AD9 | 2018-02-21 15:07 | AD9 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-6DE43C7D7C2C4A8A9A79DD67F1AA9014"
ORIS 3 (Barry) Location MS5C | RATA | 201802201805AD9 | 2018-02-21 15:07 | AD9 (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-6DE43C7D7C2C4A8A9A79DD67F1AA9014"
ORIS 3 (Barry) Location MS5C | RATA | 201802201805AD9 | 2018-02-21 15:07 | AD9 (FLOW) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-6DE43C7D7C2C4A8A9A79DD67F1AA9014"
ORIS 3 (Barry) Location MS5C | RATA | 201902200950AD6 | 2019-02-20 17:19 | AD6 (SO2) | CRIT2 | RATA-38-A | Fired | The average gross unit load recalculated from the values in the run records for Operating Level L is not within the low level operating range defined in the load record. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-27EC6BBC66744C2FAFBE30775EEE0C3B"
ORIS 3 (Barry) Location MS5C | RATA | 201902200950AD6 | 2019-02-20 17:19 | AD6 (SO2) | CRIT2 | RATA-47-E | Fired | The load level for this RATA was not designated as a normal load level in the active load record. |  | "QAT" "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-27EC6BBC66744C2FAFBE30775EEE0C3B"
ORIS 3 (Barry) Location MS5C | RATA | 201902200950AD6 | 2019-02-20 17:19 | AD6 (SO2) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-27EC6BBC66744C2FAFBE30775EEE0C3B"
ORIS 3 (Barry) Location MS5C | RATA | 201902200950AD6 | 2019-02-20 17:19 | AD6 (SO2) | INFORM | RATA-132-A | Fired | You have reported more than 3 decimal places for ConfidenceCoefficient, MeanCEMValue, MeanDifference, MeanRATAReferenceValue, and StandardDeviationDifference, which is not permitted by Part 75. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-27EC6BBC66744C2FAFBE30775EEE0C3B"
ORIS 3 (Barry) Location MS5C | RATA | 201902200950AD6 | 2019-02-20 17:19 | AD6 (SO2) | INFORM | TEST-21-A | Fired | IMPORTANT FYI: This test was determined to be "INVALID" due to one or more Critical Level 2 errors. The reported data indicate that the test was not performed according to the requirements and therefore cannot be used to validate emissions data. Unless you make corrections to the test data and re-run the evaluation, this test will be disregarded by the emissions evaluation routine. If you are unable to eliminate the Critical Level 2 error(s) by correcting the test data but you believe this test should be considered valid, contact your CAMD analyst. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-27EC6BBC66744C2FAFBE30775EEE0C3B"
ORIS 3 (Barry) Location MS5C | RATA | 201902211047AD9 | 2019-02-21 11:36 | AD9 (FLOW) | CRIT1 | RATA-47-C | Fired | You did not perform the test for one or both of the operating levels that were designated as normal in the active load record. The correct BAF cannot be determined for this multi-load flow test. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-85C0926945AD4EEBACA7CC62811FCD12"
ORIS 3 (Barry) Location MS5C | RATA | 201902211047AD9 | 2019-02-21 11:36 | AD9 (FLOW) | CRIT1 | RATA-51-C | Fired | The reported OverallBiasAdjustmentFactor is inconsistent with the BAF recalculated by EPA. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-85C0926945AD4EEBACA7CC62811FCD12"
ORIS 3 (Barry) Location MS5C | RATA | 201902211047AD9 | 2019-02-21 11:36 | AD9 (FLOW) | CRIT2 | RATA-38-A | Fired | The average gross unit load recalculated from the values in the run records for Operating Level L is not within the low level operating range defined in the load record. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-85C0926945AD4EEBACA7CC62811FCD12"
ORIS 3 (Barry) Location MS5C | RATA | 201902211047AD9 | 2019-02-21 11:36 | AD9 (FLOW) | CRIT2 | RATA-38-C | Fired | The average gross unit load recalculated from the values in the run records for Operating Level H is not within the high level operating ranges defined in the load record. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-85C0926945AD4EEBACA7CC62811FCD12"
ORIS 3 (Barry) Location MS5C | RATA | 201902211047AD9 | 2019-02-21 11:36 | AD9 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-85C0926945AD4EEBACA7CC62811FCD12"
ORIS 3 (Barry) Location MS5E | RATA | 201405280733AE4 | 2014-05-28 14:51 | AE4 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-F2D46DC42B104F959F4BE8E26ABC1C06"
ORIS 3 (Barry) Location MS5E | RATA | 201512011045AE4 | 2015-12-01 11:36 | AE4 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "TWCORNEL5-EA112F04E50E44E29ED6A63A025E4B4F" "TWCORNEL5-FA26A31CECDD4FAFAD4C5912D42E3B18"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2018-001 | 2018-09-20 11:13 | 107 (FLOW) | CRIT1 | RATA-76-B | Fired | You provided both an AvgVelDiffPressure and AvgSquareVelDiffPressure for Operating Level L Run Number 6 Traverse Point ID CC4. Report only one of these two values for each traverse point. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-CC4638E88BCA48C29A98794F964A6F32"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2018-001 | 2018-09-20 11:13 | 107 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID CC4 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-CC4638E88BCA48C29A98794F964A6F32"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2018-001 | 2018-09-20 11:13 | 107 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level L, because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-CC4638E88BCA48C29A98794F964A6F32"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2018-001 | 2018-09-20 11:13 | 107 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-CC4638E88BCA48C29A98794F964A6F32"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2018-001 | 2018-09-20 11:13 | 107 (FLOW) | INFORM | RATA-80-B | Fired | Recalculation of the CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID CC4 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-CC4638E88BCA48C29A98794F964A6F32"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2018-001 | 2018-09-20 11:13 | 107 (FLOW) | INFORM | RATA-87-A | Fired | Recalculation of the AvgVelocityWithoutWallEffects and AverageStackFlowRate for Operating Level L Run Number 6 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-CC4638E88BCA48C29A98794F964A6F32"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | CRIT1 | RATA-81-A | Fired | You reported a value of 1 as the PointUsedIndicator for Operating Level H Run Number 1 Traverse Point ID DD3, but did not provide the ReplacementVelocity. The software cannot determine if this traverse point should be used to recalculate a wall effects adjustment factor for this run. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | CRIT1 | RATA-82-A | Fired | You reported a value of 1 as the PointUsedIndicator for Operating Level H Run Number 1 Traverse Point ID DD3, but you did not report a valid value as the NumberWallEffectsPoints. Measurements at two or more wall effects points are required to determine a replacement velocity for an exterior method 1 traverse point. The software cannot determine if this traverse point should be used to recalculate a wall effects adjustment factor for this run. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | CRIT1 | RATA-83-A | Fired | You did not provide ReplacementVelocity, which is required for Operating Level H Run Number 1 Traverse Point ID DD3. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | INFORM | RATA-88-A | Fired | Recalculation of the AverageVelocityWithWallEffects and the CalculatedWAF for Operating Level H Run Number 1 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 6 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 9 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 8 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 10 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 12 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 4 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 5 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2019-001 | 2019-09-10 08:05 | 107 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 7 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-65E564C5E6CF423CBED77391B3207B4A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2020-001 | 2020-08-25 07:56 | 107 (FLOW) | CRIT1 | RATA-90-C | Fired | The AvgVelocityWithoutWallEffects for Operating Level H Run Number 1 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-218F542A7AAD42B18E9882D840581284"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2020-001 | 2020-08-25 07:56 | 107 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-218F542A7AAD42B18E9882D840581284"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2021-001 | 2021-09-15 08:27 | 107 (FLOW) | CRIT1 | RATA-12-C | Fired | The BeginDate in the single-level claim for this RATA does not correspond to the completion date of the last annual flow RATA for the system. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGEBGRESS-E82EAF0BE04C44BC80C31AA509449DAB"
ORIS 6030 (Coal Creek) Location 1 | RATA | 107-Q3-2021-001 | 2021-09-15 08:27 | 107 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGEBGRESS-E82EAF0BE04C44BC80C31AA509449DAB"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2018-001 | 2018-09-20 11:13 | 108 (FLOW) | CRIT1 | RATA-75-A | Fired | You did not provide LastProbeDate, which is required for Operating Level M Run Number 3 Traverse Point ID BB1. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-17D8C3AA1A3640F5A2A14F6CC9A0AABE"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2018-001 | 2018-09-20 11:13 | 108 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-17D8C3AA1A3640F5A2A14F6CC9A0AABE"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | CRIT1 | RATA-78-A | Fired | You did not provide YawAngle, which is required for Operating Level H Run Number 1 Traverse Point ID AA2. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID AA2 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-80-B | Fired | Recalculation of the CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID AA2 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-87-A | Fired | Recalculation of the AvgVelocityWithoutWallEffects and AverageStackFlowRate for Operating Level H Run Number 1 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 8 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 10 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 11 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 12 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 5 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 6 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 7 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2019-001 | 2019-09-10 08:05 | 108 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 9 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-2B05A0BBD0A14EAAAC42E0348E7DA90A"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2020-001 | 2020-08-25 07:56 | 108 (FLOW) | CRIT1 | RATA-92-D | Fired | The reported CalculatedWAF for Operating Level H Run Number 1 is inconsistent with the value recalculated from the velocity values. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-226FDCDD2D3243D78AAF03B739650D97"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2020-001 | 2020-08-25 07:56 | 108 (FLOW) | CRIT1 | RATA-95-D | Fired | The reported CalculatedWAF for Operating Level H is inconsistent with the value recalculated from the velocity values. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-226FDCDD2D3243D78AAF03B739650D97"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2020-001 | 2020-08-25 07:56 | 108 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-226FDCDD2D3243D78AAF03B739650D97"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2020-001 | 2020-08-25 07:56 | 108 (FLOW) | INFORM | RATA-91-A | Fired | The NumberWallEffectsPoints reported in the RATA Traverse records for Operating Level H Run Number 1 are inconsistent. Therefore, it is assumed that a partial wall effects traverse was performed. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-226FDCDD2D3243D78AAF03B739650D97"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2021-001 | 2021-09-15 08:27 | 108 (FLOW) | CRIT1 | RATA-13-A | Fired | You did not provide EndDate, which is required for Test Claim SLC. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGEBGRESS-BA7EFE1A86464C889415885343F18967"
ORIS 6030 (Coal Creek) Location 1 | RATA | 108-Q3-2021-001 | 2021-09-15 08:27 | 108 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGEBGRESS-BA7EFE1A86464C889415885343F18967"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2018-001 | 2018-09-20 11:13 | 109 (FLOW) | CRIT1 | RATA-77-B | Fired | The value 1001.0 in the field TStackTemperature for Operating Level H Run Number 1 Traverse Point ID DD4 is not within the range of valid values from 0 to 1000. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-A4C44F6EAD324323B6A9208B1FE1489B"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2018-001 | 2018-09-20 11:13 | 109 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID DD4 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-A4C44F6EAD324323B6A9208B1FE1489B"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2018-001 | 2018-09-20 11:13 | 109 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-A4C44F6EAD324323B6A9208B1FE1489B"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2018-001 | 2018-09-20 11:13 | 109 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-A4C44F6EAD324323B6A9208B1FE1489B"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2018-001 | 2018-09-20 11:13 | 109 (FLOW) | INFORM | RATA-80-B | Fired | Recalculation of the CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID DD4 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-A4C44F6EAD324323B6A9208B1FE1489B"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2018-001 | 2018-09-20 11:13 | 109 (FLOW) | INFORM | RATA-87-A | Fired | Recalculation of the AvgVelocityWithoutWallEffects and AverageStackFlowRate for Operating Level H Run Number 1 was not performed because of the errors listed above. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-A4C44F6EAD324323B6A9208B1FE1489B"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2019-001 | 2019-09-10 08:05 | 109 (FLOW) | NONCRIT | RATA-79-C | Fired | You have provided a value for PitchAngle for Operating Level H Run Number 10 Traverse Point ID BB2, which is not appropriate for a test using this reference method. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-38C150C5D6D942AFACBFE9F90697AACC"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2019-001 | 2019-09-10 08:05 | 109 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-38C150C5D6D942AFACBFE9F90697AACC"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2020-001 | 2020-08-25 07:56 | 109 (FLOW) | NONCRIT | RATA-89-B | Fired | You reported AverageVelocityWithWallEffects for Operating Level H Run Number 12, but you did not identify any exterior method 1 traverse points for this run. Four exterior method 1 traverse points are required to calculate a AverageVelocityWithWallEffects. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-CA128BCD7E9648DEA51F0502E8E2424D"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2020-001 | 2020-08-25 07:56 | 109 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGECRIEHL-CA128BCD7E9648DEA51F0502E8E2424D"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2021-001 | 2021-09-15 08:27 | 109 (FLOW) | CRIT1 | RATA-10-D | Fired | The sum of the percentages provided for Low, Mid and High load levels does not represent 100% of the range of operation. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGEBGRESS-498C82CFA41349019CEF3679C8401EB2"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2021-001 | 2021-09-15 08:27 | 109 (FLOW) | CRIT1 | RATA-11-B | Fired | The value -1.0 in the field LowLoadPercentage for Test Claim SLC is not within the range of valid values from 0 to 100. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGEBGRESS-498C82CFA41349019CEF3679C8401EB2"
ORIS 6030 (Coal Creek) Location 1 | RATA | 109-Q3-2021-001 | 2021-09-15 08:27 | 109 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-DA2CA5AD20EE47E4BDA6CC1F5EF65938" "CCGEBGRESS-498C82CFA41349019CEF3679C8401EB2"
ORIS 6030 (Coal Creek) Location 2 | RATA | 207-Q3-2021-001 | 2021-09-15 11:27 | 207 (FLOW) | CRIT1 | RATA-35-A | Fired | The values reported for RelativeAccuracy in the RATA summary record for Operating Level H are inconsistent with the values that have been recalculated from the run records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-87DDBC816B8548009E13F6F9F488FE0B"
ORIS 6030 (Coal Creek) Location 2 | RATA | 207-Q3-2021-001 | 2021-09-15 11:27 | 207 (FLOW) | CRIT1 | RATA-48-C | Fired | The OverallRelativeAccuracy reported in the RATA record is not equal to the highest relative accuracy recalculated from the run records for each operating level. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-87DDBC816B8548009E13F6F9F488FE0B"
ORIS 6030 (Coal Creek) Location 2 | RATA | 207-Q3-2021-001 | 2021-09-15 11:27 | 207 (FLOW) | CRIT1 | RATA-53-D | Fired | The TestResultCode indicates a passing test, but the relative accuracy recalculated from the run records indicates a failing test. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-87DDBC816B8548009E13F6F9F488FE0B"
ORIS 6030 (Coal Creek) Location 2 | RATA | 207-Q3-2021-001 | 2021-09-15 11:27 | 207 (FLOW) | CRIT1 | RATA-122-A | Fired | For one or more runs of this RATA the CEM Value and/or Reference Value was equal to zero. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-87DDBC816B8548009E13F6F9F488FE0B"
ORIS 6030 (Coal Creek) Location 2 | RATA | 207-Q3-2021-001 | 2021-09-15 11:27 | 207 (FLOW) | NONCRIT | RATA-40-A | Fired | The values reported for MeanDifference and MeanCEMValue in the RATA summary record for Operating Level H are inconsistent with the values that have been recalculated from the run records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-87DDBC816B8548009E13F6F9F488FE0B"
ORIS 6030 (Coal Creek) Location 2 | RATA | 207-Q3-2021-001 | 2021-09-15 11:27 | 207 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-87DDBC816B8548009E13F6F9F488FE0B"
ORIS 6030 (Coal Creek) Location 2 | RATA | 208-Q3-2021-001 | 2021-09-15 11:27 | 208 (FLOW) | CRIT1 | RATA-131-A | Fired | Your reported an APS Code for Operating Level H, which is only allowed for RATA tests on an HCl system |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-06E75542451241BE8A92119C511C9C0C"
ORIS 6030 (Coal Creek) Location 2 | RATA | 208-Q3-2021-001 | 2021-09-15 11:27 | 208 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-06E75542451241BE8A92119C511C9C0C"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2019-001 | 2019-09-10 13:04 | 209 (FLOW) | CRIT1 | RATA-94-B | Fired | You defined an invalid AverageStackFlowRate for Operating Level H Run Number 3. This value must be greater than zero and less than 20,000. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGECRIEHL-5C4E57C8FF7D4692876C44F656EB87FC"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2019-001 | 2019-09-10 13:04 | 209 (FLOW) | NONCRIT | RATA-40-A | Fired | The values reported for MeanDifference and MeanRATAReferenceValue in the RATA summary record for Operating Level H are inconsistent with the values that have been recalculated from the run records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGECRIEHL-5C4E57C8FF7D4692876C44F656EB87FC"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2019-001 | 2019-09-10 13:04 | 209 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGECRIEHL-5C4E57C8FF7D4692876C44F656EB87FC"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-35-A | Fired | The values reported for RelativeAccuracy in the RATA summary record for Operating Level H are inconsistent with the values that have been recalculated from the run records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-48-C | Fired | The OverallRelativeAccuracy reported in the RATA record is not equal to the highest relative accuracy recalculated from the run records for each operating level. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-89-C | Fired | The AverageVelocityWithWallEffects for Operating Level H Run Number 1 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-92-D | Fired | The reported CalculatedWAF for Operating Level H Run Number 1 is inconsistent with the value recalculated from the velocity values. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-95-D | Fired | The reported CalculatedWAF for Operating Level H is inconsistent with the value recalculated from the velocity values. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-98-A | Fired | The AverageStackFlowRate reported for Operating Level H Run Number 12 is inconsistent with the value recalculated from the Flow Rata Run and RATA Traverse records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-98-A | Fired | The AverageStackFlowRate reported for Operating Level H Run Number 1 is inconsistent with the value recalculated from the Flow Rata Run and RATA Traverse records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-98-A | Fired | The AverageStackFlowRate reported for Operating Level H Run Number 10 is inconsistent with the value recalculated from the Flow Rata Run and RATA Traverse records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-98-A | Fired | The AverageStackFlowRate reported for Operating Level H Run Number 11 is inconsistent with the value recalculated from the Flow Rata Run and RATA Traverse records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-98-A | Fired | The AverageStackFlowRate reported for Operating Level H Run Number 3 is inconsistent with the value recalculated from the Flow Rata Run and RATA Traverse records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-98-A | Fired | The AverageStackFlowRate reported for Operating Level H Run Number 5 is inconsistent with the value recalculated from the Flow Rata Run and RATA Traverse records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-98-A | Fired | The AverageStackFlowRate reported for Operating Level H Run Number 6 is inconsistent with the value recalculated from the Flow Rata Run and RATA Traverse records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-98-A | Fired | The AverageStackFlowRate reported for Operating Level H Run Number 8 is inconsistent with the value recalculated from the Flow Rata Run and RATA Traverse records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | CRIT1 | RATA-98-A | Fired | The AverageStackFlowRate reported for Operating Level H Run Number 9 is inconsistent with the value recalculated from the Flow Rata Run and RATA Traverse records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | NONCRIT | RATA-40-A | Fired | The values reported for MeanDifference and MeanRATAReferenceValue in the RATA summary record for Operating Level H are inconsistent with the values that have been recalculated from the run records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2020-001 | 2020-08-25 10:46 | 209 (FLOW) | INFORM | RATA-96-A | Fired | You have indicated the use of calculated wall effects adjustment factor for Operating Level H, but the WAF calculated from the data in the Flow RATA Run and RATA Traverse records is greater than .9950. It may be advantageous for you to use a default WAF in your RATA calculations. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-848EE97DC25147FE8F635476E575AEE9"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | CRIT1 | RATA-85-D | Fired | The NumberOfTraversePoints reported for Operating Level H Run Number 1 does not correspond to the number of traverse points identified in RATA Traverse records. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | INFORM | RATA-87-A | Fired | Recalculation of the AvgVelocityWithoutWallEffects and AverageStackFlowRate for Operating Level H Run Number 1 was not performed because of the errors listed above. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 6 was not performed because of the errors listed above. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 7 was not performed because of the errors listed above. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 10 was not performed because of the errors listed above. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 11 was not performed because of the errors listed above. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 12 was not performed because of the errors listed above. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 2 was not performed because of the errors listed above. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 3 was not performed because of the errors listed above. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6030 (Coal Creek) Location 2 | RATA | 209-Q3-2021-001 | 2021-09-15 11:27 | 209 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 4 was not performed because of the errors listed above. |  | QAT "MDC-BA1136E55C2244408FF2C0E1CAD1A42C" "CCGEBGRESS-FD9628E1ECB54A97AF6D9F04DED5D4F3"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-63-A | Fired | You did not provide BarometricPressure, which is required for Operating Level H Run Number 1. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 101 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 102 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 103 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 104 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 105 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 106 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 107 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 108 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 109 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 110 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 201 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 202 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 203 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 204 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 205 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 206 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 207 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 208 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 209 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 210 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 301 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 302 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 303 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 304 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 305 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 306 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 307 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 308 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 309 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 310 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 401 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 402 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 403 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 404 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 405 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 406 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 407 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 408 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 409 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 410 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-80-A | Fired | Recalculation of the CalculatedVelocity for all traverse points for operating level H, run number 1 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-87-A | Fired | Recalculation of the AvgVelocityWithoutWallEffects and AverageStackFlowRate for Operating Level H Run Number 1 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 10 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 1 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 3 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 4 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 5 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 6 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 7 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 8 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2018-001 | 2018-07-24 12:23 | 114 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 9 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-3C9D4BC2C32E44848D3D69CE7E655F8C"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-35-A | Fired | The values reported for RelativeAccuracy in the RATA summary record for Operating Level L are inconsistent with the values that have been recalculated from the run records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-48-C | Fired | The OverallRelativeAccuracy reported in the RATA record is not equal to the highest relative accuracy recalculated from the run records for each operating level. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 101 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 102 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 103 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 104 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 105 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 106 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 107 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 108 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 201 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 202 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 203 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 204 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 205 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 206 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 207 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 208 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 301 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 302 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 303 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 304 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 305 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 306 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 307 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 308 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 401 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 402 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 403 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 404 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 405 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 406 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 407 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 3 Traverse Point ID 408 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-90-C | Fired | The AvgVelocityWithoutWallEffects for Operating Level L Run Number 3 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | CRIT1 | RATA-98-A | Fired | The AverageStackFlowRate reported for Operating Level L Run Number 3 is inconsistent with the value recalculated from the Flow Rata Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | NONCRIT | RATA-40-A | Fired | The values reported for MeanDifference and MeanRATAReferenceValue in the RATA summary record for Operating Level L are inconsistent with the values that have been recalculated from the run records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2019-001 | 2019-07-16 13:35 | 114 (FLOW) | INFORM | RATA-64-C | Fired | The value 11.00 in the StackStaticPressure for Operating Level L Run Number 3 is outside the range of normally expected values. Please correct this value if it has been reported in error. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-9C7810D223E0439082716F1DF798B083"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-65-B | Fired | The value -1.0 in the field PercentCO2 for Operating Level H Run Number 11 is not within the range of valid values from 0.1 to 20.0. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 101 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 102 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 103 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 104 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 105 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 106 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 107 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 108 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 109 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 110 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 201 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 202 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 203 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 204 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 205 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 206 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 207 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 208 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 209 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 210 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 301 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 302 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 303 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 304 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 305 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 306 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 307 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 308 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 309 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 310 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 401 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 402 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 403 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 404 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 405 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 406 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 407 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 408 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 409 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 11 Traverse Point ID 410 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | INFORM | RATA-80-A | Fired | Recalculation of the CalculatedVelocity for all traverse points for operating level H, run number 11 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2020-001 | 2020-08-04 13:05 | 114 (FLOW) | INFORM | RATA-87-A | Fired | Recalculation of the AvgVelocityWithoutWallEffects and AverageStackFlowRate for Operating Level H Run Number 11 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-245C09613D614850898139609A184850"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-66-A | Fired | You did not provide PercentO2, which is required for Operating Level L Run Number 6. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 101 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 102 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 103 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 104 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 105 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 106 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 107 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 108 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 109 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 110 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 201 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 202 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 203 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 204 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 205 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 206 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 207 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 208 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 209 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 210 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 301 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 302 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 303 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 304 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 305 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 306 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 307 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 308 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 309 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 310 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 401 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 402 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 403 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 404 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 405 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 406 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 407 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 408 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 409 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level L Run Number 6 Traverse Point ID 410 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level L, because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | INFORM | RATA-80-A | Fired | Recalculation of the CalculatedVelocity for all traverse points for operating level L, run number 6 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 1 | RATA | 114-Q3-2021-001 | 2021-09-24 11:31 | 114 (FLOW) | INFORM | RATA-87-A | Fired | Recalculation of the AvgVelocityWithoutWallEffects and AverageStackFlowRate for Operating Level L Run Number 6 was not performed because of the errors listed above. |  | QAT "MDC-FB24B63F7DE1487AAF1CD65E44D05E54" "TGOSQL12SV-56AF57CCB9104AB59FACA4035B02118E"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-67-A | Fired | You did not provide PercentMoisture , which is required for Operating Level H Run Number 1. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 101 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 102 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 103 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 104 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 105 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 106 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 107 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 108 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 109 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 110 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 201 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 202 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 203 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 204 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 205 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 206 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 207 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 208 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 209 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 210 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 301 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 302 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 303 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 304 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 305 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 306 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 307 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 308 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 309 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 310 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 401 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 402 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 403 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 404 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 405 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 406 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 407 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 408 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 409 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 410 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-80-A | Fired | Recalculation of the CalculatedVelocity for all traverse points for operating level H, run number 1 was not performed because of the errors listed above. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-87-A | Fired | Recalculation of the AvgVelocityWithoutWallEffects and AverageStackFlowRate for Operating Level H Run Number 1 was not performed because of the errors listed above. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 10 was not performed because of the errors listed above. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 2 was not performed because of the errors listed above. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 3 was not performed because of the errors listed above. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 4 was not performed because of the errors listed above. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 5 was not performed because of the errors listed above. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 6 was not performed because of the errors listed above. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 7 was not performed because of the errors listed above. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2018-001 | 2018-07-19 14:10 | 214 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 9 was not performed because of the errors listed above. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1CE107DF3E404F579EC06F0BFCCE7561"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2019-001 | 2019-07-17 13:41 | 214 (FLOW) | CRIT1 | RATA-68-C | Fired | The DryMolecularWeight is inconsistent with the value recalculated from the data reported for Operating Level L Run Number 4. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-9246087283E348AB9DC5940BAADD8F61"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2019-001 | 2019-07-17 13:41 | 214 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-9246087283E348AB9DC5940BAADD8F61"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2020-001 | 2020-08-05 11:38 | 214 (FLOW) | CRIT1 | RATA-69-B | Fired | The value -1.00 in the field WetMolecularWeight for Operating Level H Run Number 3 is not within the range of valid values from 25 to 35. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1726A9527CEB4CBBB46D26E7F9EECA23"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2020-001 | 2020-08-05 11:38 | 214 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-1726A9527CEB4CBBB46D26E7F9EECA23"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2021-001 | 2021-09-22 13:50 | 214 (FLOW) | NONCRIT | RATA-70-C | Fired | The RATA Traverse record for this run contains invalid Traverse Point IDs. All Traverse Point IDs must consist of three alpha-numeric characters. See Operating Level H Run Number 3 Traverse Point ID 30. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-E693F647CA584458968A245B8A0F3902"
ORIS 6068 (Jeffrey Energy Center) Location 2 | RATA | 214-Q3-2021-001 | 2021-09-22 13:50 | 214 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-BE0266D30A844D61B585958DA7B9EEF6" "TGOSQL12SV-E693F647CA584458968A245B8A0F3902"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | CRIT1 | RATA-72-B | Fired | The ProbeTypeCode TYPE-SM in the RATA Traverse record for Operating Level H Run Number 1 Traverse Point ID 405 is not appropriate for a RATA using reference method 2FH. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 405 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-80-B | Fired | Recalculation of the CalculatedVelocity for Operating Level H Run Number 1 Traverse Point ID 405 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-87-A | Fired | Recalculation of the AvgVelocityWithoutWallEffects and AverageStackFlowRate for Operating Level H Run Number 1 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 10 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 11 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 12 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 3 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 5 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 7 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 8 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2019-001 | 2019-07-29 13:40 | 314 (FLOW) | INFORM | RATA-93-A | Fired | Recalculation of the AverageStackFlowRate for Operating Level H Run Number 9 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-76688A1100184E52A28EB5470B8AA3A1"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2020-001 | 2020-09-22 12:44 | 314 (FLOW) | CRIT1 | RATA-73-A | Fired | You did not provide PressureMeasureCode, which is required for Operating Level L Run Number 1 Traverse Point ID 404. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-0BF4BB6F47D4483CAE96B2B0D82C6F36"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2020-001 | 2020-09-22 12:44 | 314 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-0BF4BB6F47D4483CAE96B2B0D82C6F36"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2021-001 | 2021-09-29 13:08 | 314 (FLOW) | CRIT1 | RATA-74-B | Fired | The value 0.000 in the field VelocityCalibrationCoefficient for Operating Level H Run Number 3 Traverse Point ID 208 is not within the range of valid values from 0.5 to 1.5. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-350BD8E65AA94EA488EAA700A9120498"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2021-001 | 2021-09-29 13:08 | 314 (FLOW) | CRIT1 | RATA-84-C | Fired | The CalculatedVelocity for Operating Level H Run Number 3 Traverse Point ID 208 reported is not within 0.5% of the value calculated from run and point data reported in Flow RATA Run and RATA Traverse records. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-350BD8E65AA94EA488EAA700A9120498"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2021-001 | 2021-09-29 13:08 | 314 (FLOW) | INFORM | RATA-35-B | Fired | The software could not evaluate the RATA calculations reported for Operating Level H, because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-350BD8E65AA94EA488EAA700A9120498"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2021-001 | 2021-09-29 13:08 | 314 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-350BD8E65AA94EA488EAA700A9120498"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2021-001 | 2021-09-29 13:08 | 314 (FLOW) | INFORM | RATA-80-B | Fired | Recalculation of the CalculatedVelocity for Operating Level H Run Number 3 Traverse Point ID 208 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-350BD8E65AA94EA488EAA700A9120498"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q3-2021-001 | 2021-09-29 13:08 | 314 (FLOW) | INFORM | RATA-87-A | Fired | Recalculation of the AvgVelocityWithoutWallEffects and AverageStackFlowRate for Operating Level H Run Number 3 was not performed because of the errors listed above. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-350BD8E65AA94EA488EAA700A9120498"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q4-2018-002 | 2018-10-23 16:31 | 314 (FLOW) | CRIT1 | RATA-71-A | Fired | You did not provide ProbeID, which is required for Operating Level L Run Number 12 Traverse Point ID 305. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-AD19AE8813B0455CAE544E0F2AA0102F"
ORIS 6068 (Jeffrey Energy Center) Location 3 | RATA | 314-Q4-2018-002 | 2018-10-23 16:31 | 314 (FLOW) | INFORM | RATA-49-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-F33C839459EE443ABBE35920852434DD" "TGOSQL12SV-AD19AE8813B0455CAE544E0F2AA0102F"

## UNITDEF
Location | Test Type | Test Number | Test Date-Time | Sys/Comp Info | Severity | EASEY Result Code | Fired | EASEY Result | Notes | Command Line Parameters
ORIS 47 (Colbert) Location CCT1 | UNITDEF | LME_DSL_2Q2018 | 2018-05-01 09:48 |  | CRIT1 | UNITDEF-4-A | Fired | You did not provide TestReasonCode, which is required for this test. |  | QAT "MDC-543309AB0D4C441EB147C1CDB4953774" "NOTSET-1E7BF099EA1D4083B93C7E2978059892"
ORIS 47 (Colbert) Location CCT1 | UNITDEF | LME_DSL_2Q2018 | 2018-05-01 09:48 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-543309AB0D4C441EB147C1CDB4953774" "NOTSET-1E7BF099EA1D4083B93C7E2978059892"
ORIS 47 (Colbert) Location CCT1 | UNITDEF | LME_PNG_2Q2018 | 2018-05-01 13:31 |  | CRIT1 | UNITDEF-5-B | Fired | The value -1.000 in the field NOxDefaultRate for this test is not within the range of valid values. This value must be greater than or equal to zero. |  | QAT "MDC-543309AB0D4C441EB147C1CDB4953774" "NOTSET-22199A4311F74AD3B194FAAB4B00E6F0"
ORIS 47 (Colbert) Location CCT1 | UNITDEF | LME_PNG_2Q2018 | 2018-05-01 13:31 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-543309AB0D4C441EB147C1CDB4953774" "NOTSET-22199A4311F74AD3B194FAAB4B00E6F0"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | LME_DSL_2Q2018 | 2018-05-03 09:32 |  | CRIT1 | UNITDEF-8-C | Fired | You reported a value in NumberOfUnitsInGroup for this test, but you did not report a GroupID. This field only applies to a test that is conducted for a group of identical units. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "NOTSET-6BB1BDA0F5D741FC80AEB9904DAFB774"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | LME_DSL_2Q2018 | 2018-05-03 09:32 |  | CRIT1 | UNITDEF-9-C | Fired | You reported a value in NumberOfTestsForGroup for this test, but you did not report a GroupID. This field only applies to a test that is conducted for a group of identical units. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "NOTSET-6BB1BDA0F5D741FC80AEB9904DAFB774"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | LME_DSL_2Q2018 | 2018-05-03 09:32 |  | CRIT1 | UNITDEF-26-B | Fired | The unit-and-fuel specific NOx emission rate reported in the Monitor Default record in your monitoring plan does not correspond to the default NOx emission rate recalculated from the run values in this test. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "NOTSET-6BB1BDA0F5D741FC80AEB9904DAFB774"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | LME_DSL_2Q2018 | 2018-05-03 09:32 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "NOTSET-6BB1BDA0F5D741FC80AEB9904DAFB774"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | LME_PNG_2Q2018 | 2018-05-03 13:09 |  | CRIT1 | UNITDEF-10-A | Fired | You reported a test Begin Date, Hour, and Minute that is not the same as the BeginDate, Hour, and Minute of the first run in the test. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "NOTSET-21EABE3135DD4EEAAB98B6C678FAEBC2"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | LME_PNG_2Q2018 | 2018-05-03 13:09 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "NOTSET-21EABE3135DD4EEAAB98B6C678FAEBC2"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-GAS-2012 | 2011-11-30 10:51 |  | CRIT1 | PGVP-7-A | Fired | You did not report Protocol Gas records for all three gas levels for all reference gases used in the test. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-AFD49503F1CE4AEFAE1C4AF44BC00EF8"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-GAS-2012 | 2011-11-30 10:51 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-AFD49503F1CE4AEFAE1C4AF44BC00EF8"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-GAS-2012 | 2011-11-30 10:51 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-AFD49503F1CE4AEFAE1C4AF44BC00EF8"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-GAS-2012 | 2011-11-30 10:51 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-AFD49503F1CE4AEFAE1C4AF44BC00EF8"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-GAS-2012 | 2011-11-30 10:51 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-AFD49503F1CE4AEFAE1C4AF44BC00EF8"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-GAS-2012 | 2011-11-30 10:51 |  | CRIT1 | TEST-7-A | Fired | You reported EndDate, EndHour, and EndMinute which is prior to or equal to BeginDate, BeginHour, and BeginMinute for this test. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-AFD49503F1CE4AEFAE1C4AF44BC00EF8"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-GAS-2012 | 2011-11-30 10:51 |  | CRIT1 | UNITDEF-11-A | Fired | You reported a test EndDate, Hour, and Minute that is not the same as the EndDate, Hour, and Minute of the last run in the test. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-AFD49503F1CE4AEFAE1C4AF44BC00EF8"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-GAS-2012 | 2011-11-30 10:51 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-AFD49503F1CE4AEFAE1C4AF44BC00EF8"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-30 14:42 |  | CRIT1 | PGVP-7-A | Fired | You did not report Protocol Gas records for all three gas levels for all reference gases used in the test. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-BCD5EB3276594732920D5DD4608758E5"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-30 14:42 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-BCD5EB3276594732920D5DD4608758E5"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-30 14:42 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-BCD5EB3276594732920D5DD4608758E5"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-30 14:42 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-BCD5EB3276594732920D5DD4608758E5"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-30 14:42 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-BCD5EB3276594732920D5DD4608758E5"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-30 14:42 |  | CRIT1 | UNITDEF-13-A | Fired | One or more runs in this test have overlapping run times. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-BCD5EB3276594732920D5DD4608758E5"
ORIS 47 (Colbert) Location CCT2 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-30 14:42 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-97B373B8EC1245EB986354DCC390693D" "22BXS71-BCD5EB3276594732920D5DD4608758E5"
ORIS 47 (Colbert) Location CCT4 | UNITDEF | AAA | 2018-05-02 09:30 |  | CRIT1 | PGVP-7-B | Fired | You did not report any valid Protocol Gas records for this test. This information is required by the Protocol Gas Verification Program reporting rule. |  | QAT "MDC-672E61C5587542AD826B817C96997CC9" "CHV-LGIANN-1DE3CD6352CF4238A6B7A1C78FD89C77"
ORIS 47 (Colbert) Location CCT4 | UNITDEF | AAA | 2018-05-02 09:30 |  | CRIT1 | UNITDEF-14-A | Fired | The test was conducted at the same time as another Unit Default test with the same FuelCode and OperatingConditionCode. |  | QAT "MDC-672E61C5587542AD826B817C96997CC9" "CHV-LGIANN-1DE3CD6352CF4238A6B7A1C78FD89C77"
ORIS 47 (Colbert) Location CCT4 | UNITDEF | AAA | 2018-05-02 09:30 |  | CRIT1 | UNITDEF-24-A | Fired | You have not reported a RunUsedIndicator of 1 in any runs of this test, which indicate the runs used to calculate the default NOx emissions rate. |  | QAT "MDC-672E61C5587542AD826B817C96997CC9" "CHV-LGIANN-1DE3CD6352CF4238A6B7A1C78FD89C77"
ORIS 47 (Colbert) Location CCT4 | UNITDEF | AAA | 2018-05-02 09:30 |  | CRIT2 | AETB-10-A | Fired | You did not report any valid Air Emission Testing records for this test. This information is required by the Air Emission Testing reporting rule. |  | QAT "MDC-672E61C5587542AD826B817C96997CC9" "CHV-LGIANN-1DE3CD6352CF4238A6B7A1C78FD89C77"
ORIS 47 (Colbert) Location CCT4 | UNITDEF | LME_DSL_2Q2018 | 2018-05-02 09:37 |  | CRIT1 | UNITDEF-14-A | Fired | The test was conducted at the same time as another Unit Default test with the same FuelCode and OperatingConditionCode. |  | QAT "MDC-672E61C5587542AD826B817C96997CC9" "NOTSET-12F6DD4451F14931AD679D3A55EF604A"
ORIS 47 (Colbert) Location CCT4 | UNITDEF | LME_DSL_2Q2018 | 2018-05-02 09:37 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-672E61C5587542AD826B817C96997CC9" "NOTSET-12F6DD4451F14931AD679D3A55EF604A"
ORIS 47 (Colbert) Location CCT4 | UNITDEF | LME_PNG_2Q2018 | 2018-05-02 13:21 |  | CRIT1 | UNITDEF-15-A | Fired | The Unit Default test contains fewer than three run records for OperatingLevelForRun 1. A minimum of three runs are required at each operating level. |  | QAT "MDC-672E61C5587542AD826B817C96997CC9" "NOTSET-4B321986853C4927BD9FBFB2C762DB3F"
ORIS 47 (Colbert) Location CCT4 | UNITDEF | LME_PNG_2Q2018 | 2018-05-02 13:21 |  | CRIT1 | UNITDEF-23-A | Fired | The Unit Default test contains fewer than three run records for OperatingLevelForRun 2. A minimum of three runs are required at each operating level. |  | QAT "MDC-672E61C5587542AD826B817C96997CC9" "NOTSET-4B321986853C4927BD9FBFB2C762DB3F"
ORIS 47 (Colbert) Location CCT4 | UNITDEF | LME_PNG_2Q2018 | 2018-05-02 13:21 |  | CRIT1 | UNITDEF-24-B | Fired | You have reported a RunUsedIndicator in runs for more than one operating level of this test. The default NOx emissions rate should only be calculated from the runs of one operating level. |  | QAT "MDC-672E61C5587542AD826B817C96997CC9" "NOTSET-4B321986853C4927BD9FBFB2C762DB3F"
ORIS 47 (Colbert) Location CCT4 | UNITDEF | LME_PNG_2Q2018 | 2018-05-02 13:21 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-672E61C5587542AD826B817C96997CC9" "NOTSET-4B321986853C4927BD9FBFB2C762DB3F"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8001 | 2003-02-20 16:03 |  | CRIT1 | UNITDEF-13-A | Fired | One or more runs in this test have overlapping run times. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-3E55BA23BA2B4B60B3FE3AC4ACAFBE2E"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8001 | 2003-02-20 16:03 |  | CRIT1 | UNITDEF-15-A | Fired | The Unit Default test contains fewer than three run records for OperatingLevelForRun -1. A minimum of three runs are required at each operating level. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-3E55BA23BA2B4B60B3FE3AC4ACAFBE2E"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8001 | 2003-02-20 16:03 |  | CRIT1 | UNITDEF-16-B | Fired | The value -1 in the field OperatingLevelForRun for Operating Level -1 Run Number 1 is not within the range of valid values from 1 to 99. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-3E55BA23BA2B4B60B3FE3AC4ACAFBE2E"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8001 | 2003-02-20 16:03 |  | CRIT1 | UNITDEF-22-A | Fired | There are missing or non-sequential OperatingLevelForRun and RunNumbers in this test. Run numbers must begin with 1 and be consecutive within the entire test or within each operating level. The lowest OperatingLevelForRun must be equal to 1. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-3E55BA23BA2B4B60B3FE3AC4ACAFBE2E"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8001 | 2003-02-20 16:03 |  | NONCRIT | UNITDEF-4-B | Fired | You did not provide TestReasonCode for this test. This information will be required for ECMPS submissions. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-3E55BA23BA2B4B60B3FE3AC4ACAFBE2E"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8001 | 2003-02-20 16:03 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-3E55BA23BA2B4B60B3FE3AC4ACAFBE2E"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8002 | 2003-02-21 07:09 |  | CRIT1 | UNITDEF-17-A | Fired | The BeginDate, BeginHour, and/or BeginMinute for Operating Level 1 Run Number 2 is invalid. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-4C3B478D04F24538B5288E1CD425A4E8"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8002 | 2003-02-21 07:09 |  | CRIT1 | UNITDEF-27-B | Fired | You have not included in your monitoring plan a default record for ParameterCode NOXR, DefaultPurposeCode LM, DefaultSourceCode TEST, FuelCode DSL, OperatingConditionCode P to report the unit-and-fuel-specific NOx emission rate for use during peak load hours that was determined by this test. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-4C3B478D04F24538B5288E1CD425A4E8"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8002 | 2003-02-21 07:09 |  | NONCRIT | UNITDEF-4-B | Fired | You did not provide TestReasonCode for this test. This information will be required for ECMPS submissions. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-4C3B478D04F24538B5288E1CD425A4E8"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8002 | 2003-02-21 07:09 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-4C3B478D04F24538B5288E1CD425A4E8"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8002 | 2003-02-21 07:09 |  | INFORM | UNITDEF-26-A | Fired | For the current test, you have not included in your monitoring plan a default record for ParameterCode NOXR, DefaultPurposeCode LM, DefaultSourceCode TEST, FuelCode DSL with the appropriate OperatingConditionCode to report the unit-and-fuel-specific NOx emission rate that was active at the time of the test. As a reminder, fuel-and-unit-specific NOx emission rates from historical testing may not be used longer than five years after the Appendix E testing was conducted. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-4C3B478D04F24538B5288E1CD425A4E8"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8003 | 2008-02-01 10:08 |  | CRIT1 | UNITDEF-18-A | Fired | The EndDate, EndHour, and/or EndMinute for Operating Level 1 Run Number 3 are invalid. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-3E4B9A21200A446B8197C2C030BF2714"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8003 | 2008-02-01 10:08 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-3E4B9A21200A446B8197C2C030BF2714"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8004 | 2008-02-01 13:13 |  | CRIT1 | UNITDEF-19-B | Fired | The value -1 in the field ResponseTime for Operating Level 1 Run Number 1 is not within the range of valid values from 0 to 800. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-D166723B833640B783DFFE9CD22782CA"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | EPA-UNITDEF-8004 | 2008-02-01 13:13 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "EPA-D166723B833640B783DFFE9CD22782CA"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-29 11:05 |  | CRIT1 | PGVP-7-A | Fired | You did not report Protocol Gas records for all three gas levels for all reference gases used in the test. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-A209A3F7E31B425B8A86E235D2278B7A"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-29 11:05 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-A209A3F7E31B425B8A86E235D2278B7A"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-29 11:05 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-A209A3F7E31B425B8A86E235D2278B7A"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-29 11:05 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-A209A3F7E31B425B8A86E235D2278B7A"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-29 11:05 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-A209A3F7E31B425B8A86E235D2278B7A"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-29 11:05 |  | CRIT1 | UNITDEF-21-A | Fired | You did not provide ReferenceValue, which is required for Operating Level 1 Run Number 1. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-A209A3F7E31B425B8A86E235D2278B7A"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-29 11:05 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-A209A3F7E31B425B8A86E235D2278B7A"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-29 16:47 |  | CRIT1 | PGVP-7-A | Fired | You did not report Protocol Gas records for all three gas levels for all reference gases used in the test. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-39E84F48BC8E4DE1A547931738F27778"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-29 16:47 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-39E84F48BC8E4DE1A547931738F27778"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-29 16:47 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-39E84F48BC8E4DE1A547931738F27778"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-29 16:47 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-39E84F48BC8E4DE1A547931738F27778"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-29 16:47 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-39E84F48BC8E4DE1A547931738F27778"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-29 16:47 |  | CRIT1 | UNITDEF-13-A | Fired | One or more runs in this test have overlapping run times. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-39E84F48BC8E4DE1A547931738F27778"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-29 16:47 |  | CRIT1 | UNITDEF-20-B | Fired | You defined an invalid RunNumber for Operating Level 1 Run Number -1. This value must be greater than zero and less than 20,000. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-39E84F48BC8E4DE1A547931738F27778"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-29 16:47 |  | CRIT1 | UNITDEF-22-A | Fired | There are missing or non-sequential OperatingLevelForRun and RunNumbers in this test. Run numbers must begin with 1 and be consecutive within the entire test or within each operating level. The lowest OperatingLevelForRun must be equal to 1. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-39E84F48BC8E4DE1A547931738F27778"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-29 16:47 |  | CRIT1 | UNITDEF-24-C | Fired | Some runs for OperatingLevelForRun 1 of this test have RunUsedIndicators equal to 1 indicating that the run was used to calculate the default NOx emissions rate, but other runs for this operating level do not have RunUsedIndicators equal to 1. The default NOx emissions rate must be calculated from all the runs of one operating level. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-39E84F48BC8E4DE1A547931738F27778"
ORIS 47 (Colbert) Location CCT5 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-29 16:47 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-882384FA083A4AC1999E8B426E31224E" "22BXS71-39E84F48BC8E4DE1A547931738F27778"
ORIS 47 (Colbert) Location CCT6 | UNITDEF | EPA-UNITDEF-8003 | 2008-01-31 10:08 |  | CRIT1 | UNITDEF-25-A | Fired | The DefaultNOxRate reported for the test is not equal to the emissions rate recalculated from the run records. |  | QAT "MDC-4F678D297BA548759B040372B68D5F49" "EPA-4EF877932345449D992115E6E82E7058"
ORIS 47 (Colbert) Location CCT6 | UNITDEF | EPA-UNITDEF-8003 | 2008-01-31 10:08 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-4F678D297BA548759B040372B68D5F49" "EPA-4EF877932345449D992115E6E82E7058"
ORIS 47 (Colbert) Location CCT7 | UNITDEF | EPA-UNITDEF-8003 | 2021-02-05 09:35 |  | CRIT1 | PGVP-7-B | Fired | You did not report any valid Protocol Gas records for this test. This information is required by the Protocol Gas Verification Program reporting rule. |  | QAT "MDC-5B6DA3C59F99415E965C54317AE0257C" "EPA-7F604E2387CA4D1E997CA830305C23CB"
ORIS 47 (Colbert) Location CCT7 | UNITDEF | EPA-UNITDEF-8003 | 2021-02-05 09:35 |  | CRIT2 | AETB-10-A | Fired | You did not report any valid Air Emission Testing records for this test. This information is required by the Air Emission Testing reporting rule. |  | QAT "MDC-5B6DA3C59F99415E965C54317AE0257C" "EPA-7F604E2387CA4D1E997CA830305C23CB"
ORIS 47 (Colbert) Location CCT7 | UNITDEF | EPA-UNITDEF-8003 | 2021-02-05 09:35 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-5B6DA3C59F99415E965C54317AE0257C" "EPA-7F604E2387CA4D1E997CA830305C23CB"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-28 11:00 |  | CRIT1 | PGVP-7-A | Fired | You did not report Protocol Gas records for all three gas levels for all reference gases used in the test. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-2FC53FBC318F45B3BE3FABCBFE4FC533"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-28 11:00 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-2FC53FBC318F45B3BE3FABCBFE4FC533"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-28 11:00 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-2FC53FBC318F45B3BE3FABCBFE4FC533"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-28 11:00 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-2FC53FBC318F45B3BE3FABCBFE4FC533"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-28 11:00 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-2FC53FBC318F45B3BE3FABCBFE4FC533"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-GAS-2012 | 2012-11-28 11:00 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-2FC53FBC318F45B3BE3FABCBFE4FC533"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-28 14:55 |  | CRIT1 | PGVP-7-A | Fired | You did not report Protocol Gas records for all three gas levels for all reference gases used in the test. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-E1EDC1601C6C4A099C3E366C18F2759D"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-28 14:55 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-E1EDC1601C6C4A099C3E366C18F2759D"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-28 14:55 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-E1EDC1601C6C4A099C3E366C18F2759D"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-28 14:55 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-E1EDC1601C6C4A099C3E366C18F2759D"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-28 14:55 |  | CRIT1 | PGVP-10-F | Fired | You did not report a required PGVP balance component. A single balance component is required when reporting other individual gas components. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-E1EDC1601C6C4A099C3E366C18F2759D"
ORIS 47 (Colbert) Location CCT8 | UNITDEF | UNITDEF-OIL-2012 | 2012-11-28 14:55 |  | INFORM | UNITDEF-6-C | Fired | This test has already been submitted and will not be resubmitted. If you wish to resubmit this test, please contact EPA for approval. |  | QAT "MDC-EFCADAD0F835495C95B43F3720E7E008" "22BXS71-E1EDC1601C6C4A099C3E366C18F2759D"
ORIS 2292 (Sarpy County Station) Location 1 | UNITDEF | AAA | 2020-05-02 09:37 |  | CRIT1 | UNITDEF-12-A | Fired | You have reported this unit default test to determine a unit-and-fuel specific NOX default for LME, but you do not have an active NOXM LME methodology record in your monitoring plan. |  | QAT "AA59647-0125444F24564B55918CF8399D08AFBC" "CHV-LGIANN-FD4139380242460BB6F110BBA275F7D9"
ORIS 2292 (Sarpy County Station) Location 1 | UNITDEF | AAA | 2020-05-02 09:37 |  | CRIT2 | PGVP-3-E | Fired | You have reported a VendorIdentifier for Cylinder Identifier ALM041367 of a vendor who is no longer participating in the Protocol Gas Verification Program. |  | QAT "AA59647-0125444F24564B55918CF8399D08AFBC" "CHV-LGIANN-FD4139380242460BB6F110BBA275F7D9"
ORIS 2292 (Sarpy County Station) Location 1 | UNITDEF | AAA | 2020-05-02 09:37 |  | CRIT2 | PGVP-3-E | Fired | You have reported a VendorIdentifier for Cylinder Identifier AAL21525 of a vendor who is no longer participating in the Protocol Gas Verification Program. |  | QAT "AA59647-0125444F24564B55918CF8399D08AFBC" "CHV-LGIANN-FD4139380242460BB6F110BBA275F7D9"
ORIS 2292 (Sarpy County Station) Location 1 | UNITDEF | AAA | 2020-05-02 09:37 |  | CRIT2 | PGVP-4-C | Fired | You reported an ExpirationDate for the cylinder that is prior to the date of the test for Cylinder Identifier ALM041367. |  | QAT "AA59647-0125444F24564B55918CF8399D08AFBC" "CHV-LGIANN-FD4139380242460BB6F110BBA275F7D9"
ORIS 2292 (Sarpy County Station) Location 1 | UNITDEF | AAA | 2020-05-02 09:37 |  | CRIT2 | PGVP-4-C | Fired | You reported an ExpirationDate for the cylinder that is prior to the date of the test for Cylinder Identifier AAL21525. |  | QAT "AA59647-0125444F24564B55918CF8399D08AFBC" "CHV-LGIANN-FD4139380242460BB6F110BBA275F7D9"
ORIS 2292 (Sarpy County Station) Location 1 | UNITDEF | AAA | 2020-05-02 09:37 |  | INFORM | UNITDEF-26-A | Fired | For the current test, you have not included in your monitoring plan a default record for ParameterCode NOXR, DefaultPurposeCode LM, DefaultSourceCode TEST, FuelCode DSL with the appropriate OperatingConditionCode to report the unit-and-fuel-specific NOx emission rate that was active at the time of the test. As a reminder, fuel-and-unit-specific NOx emission rates from historical testing may not be used longer than five years after the Appendix E testing was conducted. |  | QAT "AA59647-0125444F24564B55918CF8399D08AFBC" "CHV-LGIANN-FD4139380242460BB6F110BBA275F7D9"